An.E: General Facilities- Process scheme.

- E.1: Filtration.

- E.2: Softening.

- E.3: Steam production.

- E.4: Conditioning.

E.1:Filtration.

| Department | General Facilities |
| --- | --- |
| Process | Filtration |
| Operating (continuous/batch) | continuous |
| Equipment | Sand filter |
| Item | SF1-SF2 |
| Number of run/yr | - |
| Run time (h) | - |
| Number of cycles/yr | 88 |
| Cycle time (h) | - |
| Backwashing time (h) | 0,23 |
| Number of regeneration/yr | 88 |

| Water type W1: 20 m3/h | Filtration | Water type W2: 20 m3/h |  |
| --- | --- | --- | --- |
| Water type W2: 9200 l | Backwashing t=10 min | Discharge type D1: 9200 l. T [°C]=18; pH [-]=7,5; Conductivity [mS/cm]=0,19; COD [mg/l]=10; TSS [mg/l]=0. |  |
| Water type W2: 2760 l | Rinsing t=3 min | Discharge type D1:2760 l. T [°C]=18; pH [-]=7,5; Conductivity [mS/cm]=0,19; COD [mg/l]=10; TSS [mg/l]=0. |  |

E.2: Softening.

| Department | General Facilities |
| --- | --- |
| Process | Softening |
| Operating (continuous/batch) | batch |
| Equipment | Ion exchange softener |
| Item | ES1-ES2 |
| Number of run/yr | 153 |
| Run time (h) | - |
| Number of cycles/yr | - |
| Cycle time (h) | - |
| Regeneration cycle time (h) | 2 |
| Number of regeneration cycles/yr | 153+153 |

| Water type W2: 485 m3/run 14,5 m3/h | Softening | Water type W3: 485 m3/run 14,5 m3/h |  |
| --- | --- | --- | --- |
| Water type W2: 4150 l | Bed expansion t=10 min | Discharge type D1:4150 l T [°C]=20; pH [-]=7,6; Conductivity [mS/cm]=0,19; COD [mg/l]=10; TSS [mg/l]=0. |  |
| Water type W2: 37500 l Brine (120 kg NaCl): 400 l | Regeneration tTOT=90 min (brine from 15 to 40) | Discharge type D1:37900 l T [°C]=20; pH [-]=8,1; Conductivity [mS/cm]=4,06; COD [mg/l]=10; TSS [mg/l]=0. |  |
| Water type W2: 8300 l | Washing t=20 min | Discharge type D1:8300 l T [°C]=20; pH [-]=7,9; Conductivity [mS/cm]=1,06; COD [mg/l]=10; TSS [mg/l]=0. |  |

E.3:Steam production.

| Department | General Facilities |
| --- | --- |
| Process | Steam production |
| Operating (continuous/batch) | continuous |
| Equipment | boiler |
| Item | B1 |
| Number of run/yr | - |
| Run time (h) | - |
| Number of cycles/yr | - |
| Cycle time (h) | 24 |
| Working hours (h) | 5280 |

| Water type W3: 1296 l/h Solution 1: 0,30 l Solution 1: Water type W3: 25 l Deoxygenating agent (S01): 9 l Conditioning agent (S02): 16 l | Evaporator | Steam type S1: 1146 kg/h Discharge type D1: 150 l/h T [°C]=20; pH [-]=7,6; Conductivity [mS/cm]=0,19; COD [mg/l]=50; TSS [mg/l]=0. |  |
| --- | --- | --- | --- |
|  | Steam losses Evaporation 1501 l/h |  |  |

E.4: Conditioning.

| Department | General Facilities |
| --- | --- |
| Process | Conditioning |
| Operating (continuous/batch) | Continuous |
| Equipment | Compressor |
| Item | C1-C2 |
| Number of run/yr | - |
| Run time (h) | - |
| Number of cycles/yr | - |
| Cycle time (h) | - |
| Working hours (h) | 1450 |

| 1) Water type W2: 250 l/h 2) Water type W2: 250 l/h | Exchanger | Discharge type D1: 250 l/h T [°C]=25; pH [-]=7,6; Conductivity [mS/cm]=0,19; COD [mg/l]=10; TSS [mg/l]=0. |
| --- | --- | --- |

- Laboratory

- CED,Offices,Server