Contents

1.	Introduction	16

1.1.	Scope of the experimental activity	16

1.1.1.	Textile effluents	16

1.1.2.	State of the art of textile effluents treatability	17

1.1.2.1.	Phisical/chemical methods	17

1.1.2.1.1.	Coagulation/flocculation	17

1.1.2.2.	Chemical methods	17

1.1.2.2.1.	Oxidative processes	17

1.1.2.2.2.	Photochemical	18

1.1.2.2.3.	Electrochemical destruction	18

1.1.2.3.	Physical treatments	18

1.1.2.3.1.	Adsorption	18

1.1.2.3.2.	Membrane filtration	18

1.1.2.3.3.	Ion exchange	19

1.1.2.3.4.	Electrokinetic coagulation	19

1.1.2.3.5.	Evaporation	19

1.1.2.4.	Biological treatments	19

1.2.	Introduction to anaerobic treatment	19

1.2.1.	Anaerobic wastewater treatment	19

1.2.1.1.	Advantages of anaerobic treatment for pre-treatment of textile wastewaters	20

1.2.1.2.	Possibly problematic compounds	20

1.2.1.2.1.	Sulphate	20

1.2.1.2.2.	Cations	21

1.2.2.	Overview of data on anaerobic treatment of textile wastewater	22

1.2.3.	Anaerobic decolourisation of dyeing wastewater	22

1.2.3.1.	Azo dyes	24

1.2.3.2.	Anthraquinone dyes	25

1.2.4.	Application of redox mediators	27

1.3.	Introduction to membrane treatment	28

1.3.1.	Type of membranes	28

1.3.2.	Materials/geometry	28

1.3.3.	Design and evaluation	29

2.	The effluents object of the investigations	31

2.1.	Characterisation of the effluents selected for anaerobic tests	31

2.2.	Characterisation of the effluents selected for membrane tests	32

2.3.	Tests performed on the different effluents	33

3.	Material and methods	35

3.1.	Anaerobic treatment	35

3.1.1.	Anaerobic sludges used in the experiments	35

3.1.2.	Batch tests	35

3.1.2.1.	Maximum specific methanogenic activity (SMA) of the granular sludge	35

3.1.2.2.	Anaerobic degradability tests	36

3.1.2.3.	Effect of the initial wastewater concentration on anaerobic degradability	36

3.1.2.4.	Decolourisation tests	37

3.1.3.	Reactor experiments	37

3.1.3.1.	Anaerobic treatment of sizing liquid	37

3.1.3.2.	Anaerobic treatment of dyeing wastewater	39

3.1.4.	Analyses	40

3.1.4.1.	COD	40

3.1.4.2.	Colour	40

3.1.4.3.	Volatile Fatty Acids (VFA)	41

3.1.4.4.	Methane	41

3.1.4.5.	SO42-, Cl-, PO4	41

3.1.4.6.	Lipids	41

3.1.4.7.	Respirometry	42

3.2.	Membrane treatment	42

3.2.1.	The experimental equipment	42

3.2.1.1.	SDI	42

3.2.1.2.	Bench scale plant	43

3.2.1.3.	Pilot scale plant	44

3.2.1.4.	Membranes	45

3.2.2.	Analytical characterization	46

3.2.2.1.	TOC	46

3.2.2.2.	SST	47

3.2.2.3.	Conductivity	47

3.2.2.4.	Temperature	47

3.2.2.5.	pH	47

3.2.2.6.	Turbidity	47

3.2.2.7.	Colour	47

3.2.3.	Experimental activities	48

3.2.3.1.	Selection of membranes on bench scale tests	48

3.2.3.1.1.	Characterization -BS	48

3.2.3.1.2.	Complete recirculation test –BS	48

3.2.3.1.3.	Choice of the membrane	48

3.2.3.2.	Pilot scale run	49

3.2.3.2.1.	Characterization -PS	49

3.2.3.2.2.	Complete recirculation test -PS	49

3.2.3.2.3.	Concentration effect test -PS	49

3.2.3.2.4.	Second characterization –PS	50

3.2.3.2.5.	Conclusions on the pilot scale run	50

3.2.3.3.	Data elaboration	50

3.2.3.3.1.	Temperature -normalised flow rates	51

3.2.3.3.2.	TOC at growing concentration of the feed	51

3.2.3.4.	Technical/economical evaluation parameters	53

3.2.4.	Membrane cleaning and maintenance	55

3.3.	Reusability evaluations	55

3.3.1.	Pretreatment	56

3.3.1.1.	Degumming efficiency	56

3.3.1.2.	Charge efficiency	57

3.3.1.3.	Scouring efficiency	57

3.3.1.4.	Degree of whiteness	57

3.3.1.5.	Degree of polymerisation (DP)	57

3.3.2.	Dyeing	58

3.3.2.1.	Calculation of colour differences	58

3.3.2.2.	Colour fastness to washing	59

3.3.2.3.	Colour fastness to rubbing	59

3.4.	Reuse tests	60

3.4.1.	Polyester pretreatment (scouring, double scouring, rinsing)	60

3.4.1.1.	Water source	60

3.4.1.2.	Process description scouring	60

3.4.1.3.	Process description disperse dyeing	60

3.4.2.	Silk pretreatment (HT scouring, rinsing)	61

3.4.2.1.	Water source	61

3.4.2.2.	Process description pretreatment: degumming, polymer charge	61

3.4.2.3.	Process description acid dyeing	61

3.4.3.	Cotton bleaching	62

3.4.3.1.	Water source	62

3.4.3.2.	Process description bleaching	62

3.4.3.3.	Process description direct dyeing	63

3.4.4.	Disperse dyeing and printing (dyeing, printing, washing, rinsing)	63

3.4.4.1.	Reuse of disperse printing effluent	63

3.4.4.1.1.	Water source	63

3.4.4.1.2.	Process description of disperse dyeing	64

3.4.4.2.	Reuse of disperse dyeing effluent	65

3.4.4.2.1.	Water source	65

3.4.4.2.2.	Process description of scouring	65

3.4.4.2.3.	Process description of disperse dyeing	65

3.4.5.	Acid dyeing (polyamide dyeing, silk dyed rinsing)	66

3.4.5.1.	Reuse of acid dyeing effluent (polyamide dyeing)	66

3.4.5.1.1.	Water source	66

3.4.5.1.2.	Process description of acid dyeing	66

3.4.5.2.	Reuse of acid dyeing effluent (silk dyeing)	67

3.4.5.2.1.	Water source	67

3.4.5.2.2.	Process description of degumming	67

3.4.5.2.3.	Process description of acid dyeing	68

3.4.6.	Reactive dyeing	68

3.4.6.1.	Water source	68

3.4.6.2.	Process description reactive dyeing	68

3.4.6.3.	Process description direct dyeing	69

3.4.7.	Direct dyeing (viscose)	70

3.4.7.1.	Water source	70

3.4.7.2.	Process description scouring	70

3.4.7.3.	Process description direct dyeing	70

3.4.7.4.	Process description reactive dyeing	71

4.	Results and discussion	73

4.1.	Polyester pretreatment (scouring, double scouring, rinsing)	73

4.1.1.	Membrane treatment results	73

4.1.1.1.	Direct NF results	73

4.1.1.1.1.	Bench scale NF on PSR effluent	73

4.1.1.1.1.1.	Characterization of PSR/NF	73

4.1.1.1.1.2.	Complete recirculation test of PSR/NF	73

4.1.1.1.1.3.	Choice of the membrane for the pilot scale	74

4.1.1.1.2.	Pilot scale NF on PSR effluent	74

4.1.1.1.2.1.	Pi. Sc.characterization of PSR/NF	74

4.1.1.1.2.2.	Pi. Sc. complete recirculation test of PSR/NF	74

4.1.1.1.2.3.	Concentration effect test of PSR/NF	75

4.1.1.1.2.4.	Second characterization of PSR/NF	76

4.1.1.1.2.5.	Conclusions of PSR/NF	76

4.1.1.2.	UF results	78

4.1.1.2.1.	Pilot scale UF on PS effluent	78

4.1.1.2.1.1.	Pi. Sc. characterization of PS/UF	78

4.1.1.2.1.2.	Pi. Sc. complete recirculation test of PS/UF	78

4.1.1.2.1.3.	Concentration effect test of PS/UF	78

4.1.1.2.1.4.	Second characterization of PS/UF	79

4.1.1.2.1.5.	Conclusions of PS/UF	80

4.1.1.2.2.	Pilot scale UF on PDS effluent	81

4.1.1.2.2.1.	Pi. Sc. characterization of PDS/UF	81

4.1.1.2.2.2.	Pi. Sc. complete recirculation test of PDS/UF	81

4.1.1.2.2.3.	Concentration effect test of PDS/UF	82

4.1.1.2.2.4.	Second characterization of PDS/UF	83

4.1.1.2.2.5.	Conclusions of PDS/UF	83

4.1.1.3.	UF+NF results	84

4.1.1.3.1.	Pilot scale NF on PS effluent after UF	84

4.1.1.3.1.1.	Pi. Sc. characterization of PS/NF	84

4.1.1.3.1.2.	Pi. Sc. complete recirculation test of PS/NF	84

4.1.1.3.1.3.	Concentration effect test of PS/NF	85

4.1.1.3.1.4.	Second characterization of PS/NF	86

4.1.1.3.1.5.	Conclusions of PS/NF	86

4.1.1.3.2.	Pilot scale NF on PDS effluent after UF	88

4.1.1.3.2.1.	Pi. Sc. characterization of PDS/NF	88

4.1.1.3.2.2.	Pi. Sc. complete recirculation test of PDS/NF	88

4.1.1.3.2.3.	Concentration effect test of PDS/NF	88

4.1.1.3.2.4.	Second characterization of PDS/NF	89

4.1.1.3.2.5.	Conclusions of PDS/NF	90

4.1.1.4.	UF+RO results	91

4.1.1.4.1.	Pilot scale RO on PS effluent after UF	91

4.1.1.4.1.1.	Pi. Sc. characterization of PS/RO	91

4.1.1.4.1.2.	Pi. Sc. complete recirculation test of PS/ RO	91

4.1.1.4.1.3.	Concentration effect test of PS/ RO	92

4.1.1.4.1.4.	Second characterization of PS/ RO	93

4.1.1.4.1.5.	Conclusions of PS/ RO	93

4.1.1.4.2.	Pilot scale RO on PDS effluent after UF	95

4.1.1.4.2.1.	Pi. Sc. characterization of PDS/RO	95

4.1.1.4.2.2.	Pi. Sc. complete recirculation test of PDS/ RO	95

4.1.1.4.2.3.	Concentration effect test of PDS/ RO	95

4.1.1.4.2.4.	Second characterization of PDS/ RO	96

4.1.1.4.2.5.	Conclusions of PDS/ RO	97

4.1.2.	Technical - economical feasibility	98

4.1.2.1.	Cost estimation UF/PDS	99

4.1.2.2.	Cost estimation UF/PS	100

4.1.2.3.	Cost estimation UF+NF/PDS	101

4.1.2.4.	Cost estimation UF+NF/PS	102

4.1.2.5.	Cost estimation NF/PSR	103

4.1.2.6.	Cost estimation UF+RO/PDS	104

4.1.2.7.	Cost estimation UF+RO/PS	105

4.1.3.	Reuse tests results (rinsing)	106

4.1.3.1.	Reuse of scouring permeate for scouring of polyester	106

4.1.3.1.1.	Scouring efficiency	106

4.1.3.2.	Reuse of scouring permeate for disperse dyeing of polyester	106

4.1.3.2.1.	Colour differences	106

4.1.3.2.2.	Colour fastness to washing	107

4.1.3.2.3.	Colour fastness to rubbing	107

4.1.3.2.4.	Conclusions: reuse of permeate for scouring and disperse dyeing of polyester	108

4.2.	Silk pretreatment (HT scouring, rinsing)	109

4.2.1.	Membrane treatment results	109

4.2.1.1.	Direct NF results	109

4.2.1.1.1.	Bench scale NF on SSR effluent	109

4.2.1.1.1.1.	Characterization of SSR/NF	109

4.2.1.1.1.2.	Complete recirculation test of SSR/NF	109

4.2.1.1.1.3.	Choice of the membrane for the pilot scale	110

4.2.1.1.2.	Pilot scale NF on SSR effluent	110

4.2.1.1.2.1.	Pi. Sc. characterization of SSR/NF	110

4.2.1.1.2.2.	Pi. Sc. complete recirculation test of SSR/NF	110

4.2.1.1.2.3.	Concentration effect test of SSR/NF	111

4.2.1.1.2.4.	Second characterization of SSR/NF	112

4.2.1.1.2.5.	Conclusions of SSR/NF	112

4.2.1.2.	UF results	114

4.2.1.2.1.	Bench scale UF on SS effluent	114

4.2.1.2.1.1.	Characterization of SS/UF	114

4.2.1.2.1.2.	Complete recirculation test of SS/UF	114

4.2.1.2.1.3.	Choice of the membrane for the pilot scale	114

4.2.1.2.2.	Pilot scale UF of SS effluent	115

4.2.1.2.2.1.	Pi. Sc. characterization of SS/UF	115

4.2.1.2.2.2.	Pi. Sc. complete recirculation test of SS/UF	115

4.2.1.2.2.3.	Concentration effect test of SS/UF	116

4.2.1.2.2.4.	Second characterization of SS/UF	117

4.2.1.2.2.5.	Conclusions of SS/UF	117

4.2.1.3.	UF+NF results	118

4.2.1.3.1.	Bench scale NF on SS effluent after UF	118

4.2.1.3.1.1.	Characterization of SS/NF	118

4.2.1.3.1.2.	Complete recirculation test of SS/NF	118

4.2.1.3.1.3.	Choice of the membrane for the pilot scale	119

4.2.1.3.2.	Pilot scale NF (membrane DK) on SS effluent after UF	119

4.2.1.3.2.1.	Pi. Sc. characterization of SS/NF (membrane DK)	119

4.2.1.3.2.2.	Pi. Sc. complete recirculation test of SS/NF (membrane DK)	119

4.2.1.3.2.3.	Concentration effect test of SS/NF (membrane DK)	120

4.2.1.3.2.4.	Second characterization of SS/NF (membrane DK)	121

4.2.1.3.2.5.	Conclusions of SS/NF (membrane DK)	121

4.2.1.3.3.	Pilot scale NF (membrane DL) on SS effluent after UF	123

4.2.1.3.3.1.	Pi. Sc. characterization of SS/NF (membrane DL)	123

4.2.1.3.3.2.	Pi. Sc. complete recirculation test of SS/NF (membrane DL)	123

4.2.1.3.3.3.	Concentration effect test of SS/NF (membrane DL)	123

4.2.1.3.3.4.	Second characterization of SS/NF (membrane DL)	124

4.2.1.3.3.5.	Conclusions of SS/NF (membrane DL)	125

4.2.2.	Technical - economical feasibility	126

4.2.2.1.	Cost estimation UF/SS	127

4.2.2.2.	Cost estimation UF+NF/SS	128

4.2.2.3.	Cost estimation NF/SSR	129

4.2.3.	Reuse tests results (rinsing)	130

4.2.3.1.	Reuse of scouring permeate for degumming of silk	130

4.2.3.1.1.	Degumming efficiency	130

4.2.3.2.	Reuse of scouring permeate for acid dyeing of silk	130

4.2.3.2.1.	Colour differences	130

4.2.3.2.2.	Colour fastness to washing	130

4.2.3.2.3.	Colour fastness to rubbing	131

4.2.3.2.4.	Conclusions: reuse of permeate for degumming and acid dyeing of silk	132

4.3.	Cotton pretreatment (Bleaching, scouring, sizing)	133

4.3.1.	Anaerobic treatment	133

4.3.1.1.	Anaerobic biodegradability batch tests	133

4.3.1.1.1.	Sizing liquid	133

4.3.1.1.2.	Indigo dyed cotton scouring wastewater	133

4.3.1.1.3.	Bleaching wastewater	137

4.3.1.2.	Anaerobic treatment of size liquid in UASB reactor	139

4.3.1.2.1.	HRT 15 hours	139

4.3.1.2.2.	HRT 12 hours	141

4.3.1.2.3.	HRT 10 hours	142

4.3.1.2.4.	HRT 8 hours	144

4.3.1.2.5.	Maximum specific methanogenic activity of the granular sludge	147

4.3.2.	Membrane treatment results	149

4.3.2.1.	UF results	149

4.3.2.1.1.	Pilot scale UF on CBL effluent	149

4.3.2.1.1.1.	Pi. Sc. characterization of CBL/UF	149

4.3.2.1.1.2.	Pi. Sc. complete recirculation test of CBL/UF	149

4.3.2.1.1.3.	Concentration effect test of CBL/UF	150

4.3.2.1.1.4.	Second characterization of CBL/UF	150

4.3.2.1.1.5.	Conclusions of CBL/UF	150

4.3.2.2.	UF+NF results	152

4.3.2.2.1.	Pilot scale NF on CBL effluent after UF	152

4.3.2.2.1.1.	Pi. Sc. characterization of CBL/NF	152

4.3.2.2.1.2.	Pi. Sc. complete recirculation test of CBL/NF	152

4.3.2.2.1.3.	Concentration effect test of CBL/NF	152

4.3.2.2.1.4.	Second characterization of CBL/NF	153

4.3.2.2.1.5.	Conclusions of CBL/NF	153

4.3.3.	Technical - economical feasibility	155

4.3.3.1.	Cost estimation UF/CBL	156

4.3.3.2.	Cost estimation UF+NF/CBL	157

4.3.4.	Reuse tests results	158

4.3.4.1.	Reuse of bleaching permeate for cotton bleaching	158

4.3.4.1.1.	Degree of polymerisation (DP)	158

4.3.4.1.2.	Degree of whiteness	158

4.3.4.1.3.	Conclusions: reuse of permeate for bleaching cotton	158

4.3.4.2.	Reuse of bleaching permeate for direct dyeing of cotton	158

4.3.4.2.1.	Colour differences	158

4.3.4.2.2.	Colour fastness to washing	159

4.3.4.2.3.	Colour fastness to rubbing	159

4.3.4.2.4.	Conclusions: reuse of permeate for bleaching and direct dyeing of cotton	160

4.4.	Silk polymer charge	161

4.4.1.	Membrane treatment results	161

4.4.1.1.	UF results	161

4.4.1.1.1.	Bench scale UF on SPC effluent	161

4.4.1.1.1.1.	Characterization of SPC/UF	161

4.4.1.1.1.2.	Complete recirculation test of SPC/UF	161

4.4.1.1.1.3.	Choice of the membrane for the pilot scale	162

4.4.1.1.2.	Pilot scale UF (membrane MW) on SPC effluent	162

4.4.1.1.2.1.	Pi. Sc. characterization of SPC/UF (membrane MW)	162

4.4.1.1.2.2.	Pi. Sc. complete recirculation test of SPC/UF (membrane MW)	162

4.4.1.1.2.3.	Concentration effect test of SPC/UF (membrane MW)	163

4.4.1.1.2.4.	Second characterization of SPC/UF (membrane MW)	164

4.4.1.1.2.5.	Conclusions of SPC/UF (membrane MW)	164

4.4.1.1.3.	Pilot scale UF (membrane PW) on SPC effluent	165

4.4.1.1.3.1.	Pi. Sc. characterization of SPC/UF (membrane PW)	165

4.4.1.1.3.2.	Pi. Sc. complete recirculation test of SPC/UF (membrane PW)	166

4.4.1.1.3.3.	Concentration effect test of SPC/UF (membrane PW)	166

4.4.1.1.3.4.	Second characterization of SPC/UF (membrane PW)	167

4.4.1.1.3.5.	Conclusions of SPC/UF (membrane PW)	167

4.4.1.2.	UF +NF results	169

4.4.1.2.1.	Bench scale NF on SPC effluent after UF	169

4.4.1.2.1.1.	Characterization of SPC/NF	169

4.4.1.2.1.2.	Complete recirculation test of SPC/NF	169

4.4.1.2.1.3.	Choice of the membrane for the pilot scale	169

4.4.1.2.2.	Pilot scale NF on SPC effluent after UF (MW)	170

4.4.1.2.2.1.	Pi. Sc. characterization of SPC/NF on UF (MW) effluent	170

4.4.1.2.2.2.	Pi. Sc. complete recirculation test of SPC/NF on UF (MW) effluent	170

4.4.1.2.2.3.	Concentration effect test of of SPC/NF on UF (MW) effluent	170

4.4.1.2.2.4.	Second characterization of of SPC/NF on UF (MW) effluent	171

4.4.1.2.2.5.	Conclusions of of SPC/NF on UF (MW) effluent	172

4.4.1.2.3.	Pilot scale NF on SPC effluent after UF (PW)	173

4.4.1.2.3.1.	Pi. Sc. characterization of SPC/NF on UF (PW) effluent	173

4.4.1.2.3.2.	Pi. Sc. complete recirculation test of SPC/NF on UF (PW) effluent	173

4.4.1.2.3.3.	Concentration effect test of of SPC/NF on UF (PW) effluent	174

4.4.1.2.3.4.	Second characterization of of SPC/NF on UF (PW) effluent	175

4.4.1.2.3.5.	Conclusions of of SPC/NF on UF (PW) effluent	175

4.4.2.	Technical - economical feasibility	177

4.4.2.1.	Cost estimation UF/SPC	178

4.4.2.2.	Cost estimation UF+NF/SPC	179

4.5.	Disperse dyeing and printing (Polyester dyeing, printing, washing and  rinsing)	180

4.5.1.	Membrane treatment results	180

4.5.1.1.	Direct NF results	180

4.5.1.1.1.	Bench scale NF on PDDR effluent	180

4.5.1.1.1.1.	Characterization of PDDR/NF	180

4.5.1.1.1.2.	Complete recirculation test of PDDR/NF	180

4.5.1.1.1.3.	Choice of the membrane for the pilot scale	181

4.5.1.1.2.	Pilot scale NF on PDDR effluent	181

4.5.1.1.2.1.	Pi. Sc. characterization of PDDR/NF	181

4.5.1.1.2.2.	Pi. Sc. complete recirculation test of PDDR/NF	181

4.5.1.1.2.3.	Concentration effect test of PDDR/NF	182

4.5.1.1.2.4.	Second characterization of PDDR/NF	183

4.5.1.1.2.5.	Conclusions of PDDR/NF	183

4.5.1.2.	UF results	184

4.5.1.2.1.	Pilot scale UF on PDD effluent	185

4.5.1.2.1.1.	Pi. Sc. characterization of PDD/UF	185

4.5.1.2.1.2.	Pi. Sc. complete recirculation test of PDD/UF	185

4.5.1.2.1.3.	Concentration effect test of PDD/UF	185

4.5.1.2.1.4.	Second characterization of PDD/UF	186

4.5.1.2.1.5.	Conclusions of PDD/UF	187

4.5.1.2.2.	Pilot scale UF on PDP effluent	188

4.5.1.2.2.1.	Pi. Sc. characterization of PDP/UF	188

4.5.1.2.2.2.	Pi. Sc. complete recirculation test of PDP/UF	188

4.5.1.2.2.3.	Concentration effect test of PDP/UF	188

4.5.1.2.2.4.	Second characterization of PDP/UF	189

4.5.1.2.2.5.	Conclusions of PDP/UF	189

4.5.1.2.3.	Pilot scale UF on PPW effluent	190

4.5.1.2.3.1.	Pi. Sc. characterization of PPW/UF	190

4.5.1.2.3.2.	Pi. Sc. complete recirculation test of PPW/UF	191

4.5.1.2.3.3.	Concentration effect test of PPW/UF	191

4.5.1.2.3.4.	Second characterization of PPW/UF	192

4.5.1.2.3.5.	Conclusions of PPW/UF	192

4.5.1.3.	UF+NF results	194

4.5.1.3.1.	Pilot scale NF on PDD effluent after UF	194

4.5.1.3.1.1.	Pi. Sc. characterization of PDD/NF	194

4.5.1.3.1.2.	Pi. Sc. complete recirculation test of PDD/NF	194

4.5.1.3.1.3.	Concentration effect test of PDD/NF	194

4.5.1.3.1.4.	Second characterization of PDD/NF	195

4.5.1.3.1.5.	Conclusions of PDD/NF	196

4.5.1.3.2.	Pilot scale NF on PDP effluent after UF	197

4.5.1.3.2.1.	Pi. Sc. characterization of PDP/NF	197

4.5.1.3.2.2.	Pi. Sc. complete recirculation test of PDP/NF	197

4.5.1.3.2.3.	Concentration effect test of PDP/NF	198

4.5.1.3.2.4.	Second characterization of PDP/NF	198

4.5.1.3.2.5.	Conclusions of PDP/NF	199

4.5.1.3.3.	Pilot scale NF on PPW effluent after UF	200

4.5.1.3.3.1.	Pi. Sc. characterization of PPW/NF	200

4.5.1.3.3.2.	Pi. Sc. complete recirculation test of PPW/NF	200

4.5.1.3.3.3.	Concentration effect test of PPW/NF	201

4.5.1.3.3.4.	Second characterization of PPW/NF	202

4.5.1.3.3.5.	Conclusions of PPW/NF	202

4.5.1.4.	UF+RO results	204

4.5.1.4.1.	Pilot scale RO on PDD effluent after UF	204

4.5.1.4.1.1.	Pi. Sc. characterization of PDD/RO	204

4.5.1.4.1.2.	Pi. Sc. complete recirculation test of PDD/ RO	204

4.5.1.4.1.3.	Concentration effect test of PDD/ RO	204

4.5.1.4.1.4.	Second characterization of PDD/ RO	205

4.5.1.4.1.5.	Conclusions of PDD/ RO	206

4.5.1.4.2.	Pilot scale RO on PPW effluent after UF	207

4.5.1.4.2.1.	Pi. Sc. characterization of PPW/RO	207

4.5.1.4.2.2.	Pi. Sc. complete recirculation test of PPW/ RO	207

4.5.1.4.2.3.	Concentration effect test of PPW/ RO	208

4.5.1.4.2.4.	Second characterization of PPW/ RO	209

4.5.1.4.2.5.	Conclusions of PPW/ RO	209

4.5.2.	Technical - economical feasibility	211

4.5.2.1.	Cost estimation UF/PDD	212

4.5.2.2.	Cost estimation UF/PDP	213

4.5.2.3.	Cost estimation UF/PPW	214

4.5.2.4.	Cost estimation UF+NF/PDD	215

4.5.2.5.	Cost estimation UF+NF/PDP	216

4.5.2.6.	Cost estimation UF+NF/PPW	217

4.5.2.7.	Cost estimation NF/PDDR	218

4.5.2.8.	Cost estimation UF+RO/PDD	219

4.5.2.9.	Cost estimation UF+RO/PPW	220

4.5.3.	Reuse tests results (dyeing rinsing and printing)	221

4.5.3.1.	Reuse of disperse printing effluent	221

4.5.3.1.1.	Colour differences	221

4.5.3.1.2.	Colour fastness to washing	221

4.5.3.1.3.	Colour fastness to rubbing	221

4.5.3.1.4.	Conclusions: reuse of permeate for disperse dyeing of polyester	222

4.5.3.2.	Reuse of disperse dyeing effluent	222

4.5.3.2.1.	Scouring efficiency	222

4.5.3.2.2.	Colour differences	222

4.5.3.2.3.	Colour fastness to washing	223

4.5.3.2.4.	Colour fastness to rubbing	223

4.5.3.2.5.	Conclusions: reuse of permeate for scouring and disperse dyeing of polyester	224

4.6.	Acid dyeing (Polyamide dyeing and silk dyed rinsing)	225

4.6.1.	Anaerobic tests results (Polyamide dyeing)	225

4.6.1.1.	Results of batch experiments	225

4.6.1.1.1.	Mesophilic and thermophilic decolourisation with VFA-Glucose as cosubstrate	226

4.6.1.1.2.	The effect of AQS on meso- and thermophilic decolourisation with VFA-Glucose	226

4.6.1.1.3.	Decolourisation with size as cosubstrate in presence and absence of AQS	227

4.6.1.1.4.	Comparison of co-substrates and AQS concentration	227

4.6.1.2.	Control experiment for possible biological activity of size	227

4.6.1.3.	Results of the continuous experiment	230

4.6.2.	Membrane treatment results	231

4.6.2.1.	Direct NF results	231

4.6.2.1.1.	Bench scale NF on SADR effluent	231

4.6.2.1.1.1.	Characterization of SADR/NF	231

4.6.2.1.1.2.	Complete recirculation test of SADR/NF	231

4.6.2.1.1.3.	Choice of the membrane for the pilot scale	232

4.6.2.1.2.	Pilot scale NF on SADR effluent	232

4.6.2.1.2.1.	Pi. Sc. characterization of SADR/NF	232

4.6.2.1.2.2.	Pi. Sc. complete recirculation test of SADR/NF	232

4.6.2.1.2.3.	Concentration effect test of SADR/NF	232

4.6.2.1.2.4.	Second characterization of SADR/NF	233

4.6.2.1.2.5.	Conclusions of SADR/NF	234

4.6.2.2.	UF results	235

4.6.2.2.1.	Pilot scale UF on PAD effluent	235

4.6.2.2.1.1.	Pi. Sc. characterization of PAD/UF	235

4.6.2.2.1.2.	Pi. Sc. complete recirculation test of PAD/UF	235

4.6.2.2.1.3.	Concentration effect test of PAD/UF	236

4.6.2.2.1.4.	Second characterization of PAD/UF	236

4.6.2.2.1.5.	Conclusions of PAD/UF	237

4.6.2.3.	UF +NF results	238

4.6.2.3.1.	Pilot scale NF on PAD effluent after UF	238

4.6.2.3.1.1.	Pi. Sc. characterization of PAD/NF	238

4.6.2.3.1.2.	Pi. Sc. complete recirculation test of PAD/NF	238

4.6.2.3.1.3.	Concentration effect test of PAD/NF (membrane DK)	238

4.6.2.3.1.4.	Second characterization of PAD/NF	239

4.6.2.3.1.5.	Conclusions of PAD/NF	239

4.6.2.4.	Anaerobically pretreated PAD -direct NF results	241

4.6.2.4.1.	Pilot scale NF on PAD effluent anaerobically pretreated	241

4.6.2.4.1.1.	Pi. Sc. characterization of PAD/NF after anaer. treatm.	241

4.6.2.4.1.2.	Pi. Sc. complete recirculation test of PAD/NF after anaer. treatm.	241

4.6.2.4.1.3.	Concentration effect test of PAD/NF after anaer. treatm.	242

4.6.2.4.1.4.	Second characterization of PAD/NF after anaer. treatm.	242

4.6.2.4.1.5.	Conclusions of PAD/NF after anaer. treatm.	243

4.6.2.5.	Anaerobically pretreated PAD -UF results	244

4.6.2.5.1.	Pilot scale UF on PAD effluent anaerobically pretreated	244

4.6.2.5.1.1.	Pi. Sc. characterization of PAD/UF anaerobically pretreated	244

4.6.2.5.1.2.	Pi. Sc. complete recirculation test of PAD/UF anaerobically pretreated	244

4.6.2.5.1.3.	Concentration effect test of PAD/UF anaerobically pretreated	245

4.6.2.5.1.4.	Second characterization of PAD/UF anaerobically pretreated	245

4.6.2.5.1.5.	Conclusions of PAD/UF anaerobically pretreated	246

4.6.2.6.	Anaerobically pretreated PAD -UF+NF results	247

4.6.2.6.1.	Pilot scale NF on anaerobically pretreated PAD effluent after UF	247

4.6.2.6.1.1.	Pi. Sc. characterization of anaerobically pretreated PAD/NF after UF	247

4.6.2.6.1.2.	Pi. Sc. complete recirculation test of anaerobically pretreated PAD/NF after UF	247

4.6.2.6.1.3.	Concentration effect test of anaerobically pretreated PAD/NF after UF	248

4.6.2.6.1.4.	Second characterization of anaerobically pretreated PAD/NF after UF	248

4.6.2.6.1.5.	Conclusions of anaerobically pretreated PAD/NF after UF	248

4.6.3.	Assessment of changes in aerobic biodegradability using respirometry	250

4.6.4.	Tech./econ. feasibility of anaerobic treatment	251

4.6.5.	Tech./econ. feasibility of membrane treatment	252

4.6.5.1.	Cost estimation UF/PAD	253

4.6.5.2.	Cost estimation UF+NF/PAD	254

4.6.5.3.	Cost estimation NF/SADR	255

4.6.5.4.	Cost estimation UF/PADa	256

4.6.5.5.	Cost estimation UF+NF/PADa	257

4.6.5.6.	Cost estimation NF/PADa	258

4.6.6.	Reuse tests results (dyeing rinsing and printing)	259

4.6.6.1.	Reuse of acid dyeing effluent (polyamide)	259

4.6.6.1.1.	Colour differences	259

4.6.6.1.2.	Colour fastness to washing	259

4.6.6.1.3.	Colour fastness to rubbing	259

4.6.6.1.4.	Conclusions: reuse of permeate for acid dyeing of polyamide	260

4.6.6.2.	Reuse of acid dyeing effluent (silk dyeing)	260

4.6.6.2.1.	Degumming efficiency	260

4.6.6.2.2.	Colour differences	260

4.6.6.2.3.	Colour fastness to washing	261

4.6.6.2.4.	Colour fastness to rubbing	261

4.6.6.2.5.	Conclusions: reuse of permeate for degumming and acid dyeing of silk	262

4.7.	Reactive dyeing and printing(Viscose printed washing, Silk yarn dyeing and Cotton dyeing)	263

4.7.1.	Anaerobic tests results (Cotton Dyeing)	263

4.7.1.1.	Results of batch experiments	263

4.7.1.1.1.	Meso- and thermophilic decolourisation with VFA-Glucose as cosubstrate	264

4.7.1.1.2.	Effect of AQS on meso and thermophilic decolourisation with VFA-Glucose	264

4.7.1.1.3.	Decolourisation with size as cosubstrate in presence and absence of AQS	265

4.7.1.1.4.	Comparison of co-substrates and AQS concentration	265

4.7.1.2.	Results of the continuous experiment	268

4.7.2.	Membrane treatment results	269

4.7.2.1.	Direct NF results	269

4.7.2.1.1.	Bench scale NF on VRPW effluent	269

4.7.2.1.1.1.	Characterization of VRPW/NF	269

4.7.2.1.1.2.	Complete recirculation test of VRPW/NF	269

4.7.2.1.1.3.	Choice of the membrane for the pilot scale	270

4.7.2.1.2.	Pilot scale NF on VRPW effluent	270

4.7.2.1.2.1.	Pi. Sc. characterization of VRPW/NF	270

4.7.2.1.2.2.	Pi. Sc. complete recirculation test of VRPW/NF	270

4.7.2.1.2.3.	Concentration effect test of VRPW/NF	271

4.7.2.1.2.4.	Second characterization of VRPW/NF	272

4.7.2.1.2.5.	Conclusions of VRPW/NF	272

4.7.2.2.	UF results	273

4.7.2.2.1.	Pilot scale UF on VRPW effluent	273

4.7.2.2.1.1.	Pi. Sc. characterization of VRPW/UF	274

4.7.2.2.1.2.	Pi. Sc. complete recirculation test of VRPW/UF	274

4.7.2.2.1.3.	Concentration effect test of VRPW/UF	274

4.7.2.2.1.4.	Second characterization of VRPW/UF	275

4.7.2.2.1.5.	Conclusions of VRPW/UF	276

4.7.2.2.2.	Bench scale UF on SYRD effluent	277

4.7.2.2.2.1.	Characterization of SYRD/UF	277

4.7.2.2.2.2.	Complete recirculation test of SYRD/UF	277

4.7.2.2.2.3.	Choice of the membrane for the pilot scale	278

4.7.2.2.3.	Pilot scale UF on SYRD effluent	278

4.7.2.2.3.1.	Pi. Sc. characterization of SYRD/UF	278

4.7.2.2.3.2.	Pi. Sc. complete recirculation test of SYRD/UF	278

4.7.2.2.3.3.	Concentration effect test of SYRD/UF	279

4.7.2.2.3.4.	Second characterization of SYRD/UF	280

4.7.2.2.3.5.	Conclusions of SYRD/UF	280

4.7.2.2.4.	Pilot scale UF on CRD effluent	281

4.7.2.2.4.1.	Pi. Sc. characterization of CRD/UF	281

4.7.2.2.4.2.	Pi. Sc. complete recirculation test of CRD/UF	282

4.7.2.2.4.3.	Concentration effect test of CRD/UF	282

4.7.2.2.4.4.	Second characterization of CRD/UF	283

4.7.2.2.4.5.	Conclusions of CRD/UF	283

4.7.2.3.	UF +NF results	284

4.7.2.3.1.	Pilot scale NF on VRPW after UF	284

4.7.2.3.1.1.	Pi. Sc. characterization of VRPW/NF	284

4.7.2.3.1.2.	Pi. Sc. complete recirculation test of VRPW /NF	285

4.7.2.3.1.3.	Concentration effect test of VRPW/NF	285

4.7.2.3.1.4.	Second characterization of VRPW/NF	286

4.7.2.3.1.5.	Conclusions of VRPW/NF	286

4.7.2.3.2.	Bench scale NF on SYRD effluent after UF	288

4.7.2.3.2.1.	Characterization of SYRD/NF	288

4.7.2.3.2.2.	Complete recirculation test of SYRD/NF	288

4.7.2.3.2.3.	Choice of the membrane for the pilot scale	289

4.7.2.3.3.	Pilot scale NF (membrane DK) on SYRD after UF	289

4.7.2.3.3.1.	Pi. Sc. characterization of SYRD/NF (membrane DK)	289

4.7.2.3.3.2.	Pi. Sc. complete recirculation test of SYRD/NF (membrane DK)	289

4.7.2.3.3.3.	Concentration effect test of SYRD/NF (membrane DK)	289

4.7.2.3.3.4.	Second characterization of SYRD/NF (membrane DK)	290

4.7.2.3.3.5.	Conclusions of SYRD/NF (membrane DK)	291

4.7.2.3.4.	Pilot scale NF (membrane DL) on SYRD after UF	292

4.7.2.3.4.1.	Pi. Sc. characterization of SYRD/NF (membrane DL)	292

4.7.2.3.4.2.	Pi. Sc. complete recirculation test of SYRD/NF (membrane DL)	292

4.7.2.3.4.3.	Concentration effect test of SYRD/NF (membrane DL)	293

4.7.2.3.4.4.	Second characterization of SYRD/NF (membrane DL)	294

4.7.2.3.4.5.	Conclusions of SYRD/NF (membrane DL)	294

4.7.2.3.5.	Pilot scale NF on CRD after UF	296

4.7.2.3.5.1.	Pi. Sc. characterization of CRD/NF	296

4.7.2.3.5.2.	Pi. Sc. complete recirculation test of CRD/NF	296

4.7.2.3.5.3.	Concentration effect test of CRD/NF	296

4.7.2.3.5.4.	Second characterization of CRD/NF	297

4.7.2.3.5.5.	Conclusions of CRD/NF	297

4.7.2.4.	Anaerobically pretreated CRD -direct NF results	299

4.7.2.4.1.	Pilot scale NF on CRD effluent anaerobically pretreated	299

4.7.2.4.1.1.	Pi. Sc. characterization of CRD/NF after anaer. treatm.	299

4.7.2.4.1.2.	Pi. Sc. complete recirculation test of CRD/NF after anaer. treatm.	299

4.7.2.4.1.3.	Concentration effect test of CRD/NF after anaer. treatm.	300

4.7.2.4.1.4.	Second characterization of CRD/NF after anaer. treatm.	300

4.7.2.4.1.5.	Conclusions of CRD/NF after anaer. treatm.	301

4.7.2.5.	Anaerobically pretreated CRD -UF results	302

4.7.2.5.1.	Pilot scale UF on CRD effluent anaerobically pretreated	302

4.7.2.5.1.1.	Pi. Sc. characterization of CRD/UF anaerobically pretreated	302

4.7.2.5.1.2.	Pi. Sc. complete recirculation test of CRD/UF anaerobically pretreated	302

4.7.2.5.1.3.	Concentration effect test of CRD/UF anaerobically pretreated	303

4.7.2.5.1.4.	Second characterization of CRD/UF anaerobically pretreated	303

4.7.2.5.1.5.	Conclusions of CRD/UF anaerobically pretreated	303

4.7.2.6.	Anaerobically pretreated CRD -UF+NF results	304

4.7.2.6.1.	Pilot scale NF on anaerobically pretreated CRD effluent after UF	305

4.7.2.6.1.1.	Pi. Sc. characterization of anaerobically pretreated CRD/NF after UF	305

4.7.2.6.1.2.	Pi. Sc. complete recirculation test of anaerobically pretreated CRD/NF after UF	305

4.7.2.6.1.3.	Concentration effect test of anaerobically pretreated CRD/NF after UF	305

4.7.2.6.1.4.	Second characterization of anaerobically pretreated CRD/NF after UF	306

4.7.2.6.1.5.	Conclusions of anaerobically pretreated CRD/NF after UF	306

4.7.3.	Assessment of changes in aerobic biodegradability using respirometry	308

4.7.4.	Tech./econ. feasibility of anaerobic treatment	309

4.7.5.	Tech./econ. feasibility of membrane treatment	309

4.7.5.1.	Cost estimation UF/CRD	311

4.7.5.2.	Cost estimation UF/SYRD	312

4.7.5.3.	Cost estimation UF/VRPW	313

4.7.5.4.	Cost estimation UF +NF/CRD	314

4.7.5.5.	Cost estimation UF+NF/SYRD	315

4.7.5.6.	Cost estimation UF+NF/VRPW	316

4.7.5.7.	Cost estimation NF/VRPW	317

4.7.5.8.	Cost estimation UF/CRDa	318

4.7.5.9.	Cost estimation UF+NF/CRDa	319

4.7.5.10.	Cost estimation NF/CRDa	320

4.7.6.	Reuse tests results (dyeing rinsing and printing)	321

4.7.6.1.	Reuse of reactive dyeing permeate for reactive dyeing of cotton	321

4.7.6.1.1.	Colour differences	321

4.7.6.1.2.	Colour fastness to rubbing	321

4.7.6.1.3.	Colour fastness to washing	321

4.7.6.1.4.	Conclusions: reuse of permeate for reactive dyeing of cotton	322

4.7.6.2.	Reuse of reactive dyeing permeate for direct dyeing of cotton	322

4.7.6.2.1.	Colour differences	322

4.7.6.2.2.	Colour fastness to rubbing	323

4.7.6.2.3.	Colour fastness to washing	323

4.7.6.2.4.	Conclusions: reuse of permeate for direct dyeing of cotton	323

4.8.	Viscose direct dyeing rinsing	325

4.8.1.	Membrane treatment results	325

4.8.1.1.	Direct NF results	325

4.8.1.1.1.	Bench scale VDDR/NF	325

4.8.1.1.1.1.	Characterization of VDDR/NF	325

4.8.1.1.1.2.	Complete recirculation test of VDDR/NF	325

4.8.1.1.1.3.	Choice of the membrane for the pilot scale	326

4.8.1.1.2.	Pilot scale test of VDDR/NF	326

4.8.1.1.2.1.	Pi. Sc. characterization of VDDR/NF	326

4.8.1.1.2.2.	Pi. Sc. complete recirculation test of VDDR/NF	326

4.8.1.1.2.3.	Concentration effect test of VDDR/NF	326

4.8.1.1.2.4.	Second characterization of VDDR/NF	327

4.8.1.1.2.5.	Conclusions of VDDR/NF	328

4.8.2.	Technical - economical feasibility	329

4.8.2.1.	Cost estimation NF/VDDR	330

4.8.3.	Reuse tests results (dyeing rinsing and printing)	331

4.8.3.1.	Reuse of direct dyeing permeate for scouring of viscose	331

4.8.3.1.1.	Scouring efficiency	331

4.8.3.2.	Reuse of direct dyeing permeate for direct and reactive dyeing of viscose	331

4.8.3.2.1.	Colour differences	331

4.8.3.2.2.	Colour fastness to washing	332

4.8.3.2.3.	Colour fastness to rubbing	333

4.8.3.2.4.	Conclusions: reuse of permeate for scouring and dyeing of viscose	334

4.9.	Sulphur dyeing	335

4.9.1.	Anaerobic biodegradability test	335

5.	Conclusions	339

5.1.	Anaerobic treatability and feasibility of different textile waste streams	339

5.1.1.	Dyeing wastewaters	339

5.1.2.	Indigo dyed cotton scouring wastewater	339

5.1.3.	Bleaching wastewater	340

5.1.4.	Sizing liquid	340

5.2.	Anaerobic treatment of a combination of textile waste streams	340

5.3.	Anaerobic pre-treatment for membrane treatment and discharge of membrane concentrates	340

5.4.	Feasibility of membrane treatment	341

5.4.1.	UF treatment	341

5.4.2.	NF treatment	341

5.4.3.	RO treatment	341

5.5.	Reusability evaluations	342

# Introduction

## Scope of the experimental activity

The textile finishing industry is a water-intensive industry. Reclamation and reuse of water in this industrial sector is being more and more pursued and in some cases implemented.

Several treatment schemes have been successfully applied to reuse the final effluents of on site treatment plants and also of centralised ones.

The approach followed within the project TOWEF0 consists in the introduction of reclamation and reuse facilities closely integrated in the production processes. This implies working upstream and dealing with specific process effluents rather than downstream where all the effluents are mixed. In many cases this strategy was proved effective and cost saving.

The setting up of an efficient, reliable, cost-effective and “easy to operate” treatment of single wastewater streams of finishing textile industrial processes to reuse them is the objective of this research activity within the project TOWEF0. This document mainly focusses on the choice of the technology able to produce the results expected. It reports all the operational data on the treatment tests carried out (membrane filtration and anaerobic pre- treatment in some cases), their economical feasibility, the permeates reusability evaluations.

The application of the water re-use strategies proposed by the Project TOWEF0 will cause reduction in fresh water consumption and in wastewater discharge. There will always be an end-of-pipe effluent which needs treatment and its composition is expected to change significantly (quantity reduction, increase in contaminant concentration). The recalcitrance and biotoxicity of many of the components in textile wastewater that will be probably found at higher concentration in the final effluent can affect the performances of the already existing wastewater treatment plants and will influence new treatment plants design. This aspect was also investigated, as reported in Deliverable 16.

### Textile effluents

Textile finishing effluents contain contaminants, such as dispersing agents, salts, emulsifiers, levelling agents and in some cases heavy metals. Quantity and quality of the effluent streams are subject to considerable change due to the diversity in the textile processes and the wide range of chemicals employed within each industrial process.

Dyes, organic and inorganic auxiliary chemicals are widely used in all the process steps and their residues are found in the effluents affecting their colour, COD, and in some cases toxicity. The diversity in the types of industrial processes employed coupled with the wide range of chemicals and materials involved within each process cause an extreme variety in the effluents characteristics.

Process wastewater compositions vary widely due the variety of recipes, techniques, machinery, raw materials and fabrics, and this is reflected in the reported data. The textile finishing processing operations, are here briefly described:

Desizing removes the sizes applied to the yarn in the sizing operation by swelling/solubilising, hydrolysing, or oxidizing the size into a soluble form.

Scouring can be applied to both natural and synthetic materials to remove applied or natural substances.

Bleaching removes the natural yellowish colouring of cotton and other fibres, thereby increasing its whiteness. This operation is  generally required if the finished fabric is to be white or dyed a light colour.

Mercerising is performed most exclusively on pure cotton fabrics, which are treated by a concentrated caustic soda bath and a final acid wash in order to neutralise them. Its purpose is to impart lustre and also to increase dye affinity and tensile strength.

Carbonizing is performed mainly on 100% wool materials in order to remove traces of vegetable matter. Carbonizing consists of soaking the material in dilute sulphuric acid followed by drying and baking.

Fulling or Milling are mainly restricted to woollen fabrics although some worsted fabrics are milled in practice. Fulling causes the fabrics to mate and shrink and thus become denser.

Dyeing is carried out to add colour to the fabric. Identification of generic types of dye wastewaters is complicated by the diversity of both the dye chemistry and the operational modes of the dyeing process itself.

Special finishing treatments are necessary to further improve some properties or serviceability. Finishing processes involve impregnation of the fabric using a padding technique followed by a fixation step by heat. Subsequent washing may be carried out to remove residual chemicals. Properties such as soil-repellence, permanent setting, waterproof, flameproof, rotproof and mothproof are normally induced by these finishing operations.

### State of the art of textile effluents treatability

An overview of treatment processes applicable for the treatment of textile effluents is here presented. The main advantages and drawbacks are reported according to literature data. The efficiency and the feasibility of the treatment depends on the characteristics of the streams therefore the considerations here presented are valid only as general evaluations.

#### Phisical/chemical methods

##### Coagulation/flocculation

Physical-chemical reactions allow the coagulation of contaminants and their flocculation and are followed by separation of the flocs by sedimentation or filtration.

Cationic organic polymers and polyaluminiumchloride (PAC) are effective in the removal of reactive dyes.

Drawbacks are excess chemical usage, sludge production, and uncomplete dye removal

#### Chemical methods

##### Oxidative processes

This is the most commonly used method of decolourisation by chemical means. This is mainly due to its simplicity of application. The main oxidising agent is usually hydrogen peroxide (H2O2). This agent needs to be activated by some means, for example, ultra violet light.

Fentons reagent is a suitable chemical means of treating wastewaters which are resistant to biological treatment or are poisonous to live biomass. Chemical separation uses the action of sorption or bonding to remove dissolved dyes from wastewater and has been shown to be effective in decolourising both soluble and insoluble dyes. One major disadvantage of this method is sludge generation through the flocculation of the reagent and the dye molecules. Not all the dyes can be removed by Fentons treatment: cationic dyes do not coagulate at all; acid, direct, vat, mordant and reactive dyes usually coagulate, but the resulting floc and does not settle well.

Ozonation is capable of degrading chlorinated hydrocarbons, phenols, pesticides and aromatic hydrocarbons and is very effective for colour removal especially for double-bonded dye molecules. Ozonation removes a significant portion of recalcitrant COD, and improves the biodegradability of effluents. It does not increase the volume of wastewater and sludge. It can produce by-products with carcinogenic or toxic properties. Decolourisation occurs in a relatively short time. The main disadvantages of ozonation are its short half-life, typically being 20 min and the high cost.

Sodium hypochloride (NaOCl) initiates and accelerates azo-bond cleavage. This method is unsuitable for disperse dyes.. The negative effect it has is the release of aromatic amines which are carcinogenic, or otherwise toxic molecules.

##### Photochemical

This method degrades dye molecules by UV treatment in the presence of H2O2. There are advantages of photochemical treatment of dye-containing effluent; no sludge is produced and foul odours are greatly reduced. A drawback is the formation of by-products.

##### Electrochemical destruction

It has some significant advantages for use as an effective method for dye removal. There is little or no consumption of chemicals and no sludge production. The breakdown metabolites are gener ally not hazardous. It shows efficient and economical removal of dyes and degradation of recalcitrant pollutants. Drawbacks are the high costs of the electricity.

#### Physical treatments

##### Adsorption

Based on the affinity of dyes to adsorbent material. Activated carbon and low cost adsorbents (e.g. peat, fly, ash) can allow the removal of certain dyes efficiently. Adsorption can produce a high quality product, decolourisation is influenced by many physical-chemical factors, such as, dye/sorbent interaction, sorbent surface area, particle size, temperature, pH, and contact time . Drawbacks are the regeneration of adsorbents and the difficulty of prediction of the removal level.

Activated carbon is the most commonly used method of dye removal by adsorption and is very effective for adsorbing cationic, mordant, and acid dyes and to a slightly lesser extent, dispersed, direct, vat, pigment and reactive dyes. Performance is dependent on the type of carbon used and the characteristics of the wastewater. Regeneration or re-use results in a significant reduction in performance.

Cucurbituril is a cyclic polymer of glycoluril and formaldehyde. It showed verly good sorption capacity for various types of textile dyes. It is not still industrially feasible and cost is a major disadvantage.

Peat is also a good adsorbent due to cellular structure but its specific surface areas for adsorption are lower than activated carbon

Wood chips show a good adsorption capacity for acid dyes. I needs longer contact times.

##### Membrane filtration

By membrane filtration it is possible to clarify, concentrate and, most importantly, to separate dye continuously from effluent. It shows resistance to temperature, to adverse chemical environment, and to microbial attack. The disposal of concentrate, the possibility of clogging, and the capital and membrane replacement costs are its disadvantages. This method of filtration is suitable for water recycling within a textile dye plant and is able to remove all dye types.

Membrane technology has emerged as a reliable and feasible option in the treatment of various textile effluent streams. It is more flexible than alternative treatment and can allow the recovery not only of water but also of chemicals and energy and it is described in more details in paragraph 1.3.

##### Ion exchange

Both cation and anion dyes can be removed from effluent this way. Advantages of this method include no loss of adsorbent on regeneration, and the removal of soluble dyes. A major disadvantage are cost  and the poor effectiveness for disperse dyes.

##### Electrokinetic coagulation

Allows excellent removal of direct dyes from effluents but is poorly effective with acid dyes, with The high cost of the chemicals to be dosed and the production of large amounts of sludge resulting in high disposal costs are  major drawbacks.

##### Evaporation

Costs a lot because it demands large amounts of thermal energy.

#### Biological treatments

Usual activated sludge plants can remove dyes very poorly (typically no more then 30-40%. Various aerobic and anaerobic micro-organisms are capable of degrading textile dyes efficiently therefore biological treatment based on isolated microbial cultures are very promising but this technology has not yet been applied in full-scale plants.

Anaerobic bioremediation allows azo and other water-soluble dyes to be decolourised.. Anaerobic degradation of textile dyes yields only colour removal, mineralisation of compounds does not occur.

## Introduction to anaerobic treatment

### Anaerobic wastewater treatment

Anaerobic wastewater treatment is becoming more and more interesting for the treatment of industrial wastewaters. Due to the implementation of technologies for water reuse (direct or after on-site treatment) in industries, less wastewater is discharged, but with higher concentrations. This is becoming problematic for the conventional aerobic treatment systems that have been developed in a time when volumes were larger and wastewaters very diluted (Lema and Omil, 2001). Replacement of aerobic with anaerobic technology is not possible, the effluent quality of anaerobic treatment systems does not meet the requirements, therefore it has to be considered a pre-treatment technique (Lettinga et al., 1997). An extra benefit is the possible production of energy due to the formation of methane gas as the end-step in anaerobic conversions (on average 1.27·107 J/kg COD). This is in contrast with activated sludge plants, where the large energy consumption (on average 0.5–2 kW·h/kg O2) can be very costly (Lema and Omil 2001, O’Neill et al. 2000, Delée et al. 1998).

In general, when comparing a conventional aerobic treatment plant with anaerobic wastewater treatment systems the advantages of the latter are (Lema and Omil, 2001):

- Lower treatment costs, production of energy

- High flexibility, since it can be applied to very different types of effluents (higher and lower loading rates, mesophilic or thermophilic conditions, more or less complex wastewaters, etc.)

- High loading rate operation, which implies smaller space requirements (5–20 kg COD/m3.d versus 0.5–3 kg/m3.d for aerobic systems)

- Smaller volume of excess sludges

- Anaerobic organisms can be preserved unfed for a long time, which makes it possible to treat wastewaters that are generated with longer (seasonal production) or shorter (holidays and weekends) pauses in between. The sludge will remain viable, and restarting the process will only take a short time.

Anaerobic treatment systems can and will play a central role in the treatment of (industrial) wastewaters, as it is the most sustainable treatment method. Combined with appropriate pre- and post-treatment steps where necessary, anaerobic treatment will be increasingly used in (industrial) closed-cycle water systems (van Lier et al., 2001).

#### Advantages of anaerobic treatment for pre-treatment of textile wastewaters

Generally, textile wastewater is difficult to treat in activated sludge plants, due to a high organic load and the presence of dyes (Delée et al. 1998). Anaerobic treatment can be a solution for both problems. It has a low sludge production compared to aerobic systems, the capacity to decolourise the wastewater and can handle high organic loads (O’Neill 2000, Lema and Omil 2001).

Textile dyes are designed to last, and a result is that most dyes are highly resistant to aerobic degradation (Vandevivere et al. 1998). In activated sludge plants some removal occurs, through adsorption to the sludge. However, not all dyes show a good adsorption and a large fraction passes through the plant unaffected (O’Neill et al. 2000, Delée et al. 1998). Under anoxic conditions many textile dyes can be decolourised to a greater or lesser extend. Especially azo dyes (the widest used dye class) are susceptible to anaerobic treatment (Vandevivere et al. 1998, Delée et al. 1998).

#### Possibly problematic compounds

Like any process, anaerobic treatment has its drawbacks. Not all wastewaters can be treated anaerobically, and certain compounds can have a negative effect on the effectiveness of the treatment. As an example, an introduction to two of the main problematic types of compounds is given here.

##### Sulphate

The presence of sulphate in wastewater can cause problems during treatment. Sulphate itself is usually  not a problem, but the hydrogen sulphide that is formed during the anaerobic conversion of sulphate may have adverse effects. Hulshoff Pol and co-workers (1998b) provide a summary of the disadvantages and advantages of the presence of sulphate (Table 1):

Table 1 :Disadvantages and advantages of the presence of sulphate in wastewater for anaerobic treatment

| Disadvantages | Advantages |
| --- | --- |
| Reduced COD-removal efficiency due to the presence of H2S in the effluent | Removal of oxidised sulphur compounds (sulphate, sulphite and thiosulphate) from the wastestream |
| Corrosion | Precipitated metal sulphides (e.g. FeS) form good precursors for granulation |
| Accumulation of inert material in the sludge (e.g. metal sulphides) | Heavy metal removal |
| Less methane formation |  |
| Poor biogas quality + need for H2S-removal from the biogas |  |
| Malodour |  |
| Potential toxicity |  |
| Deterioration of aerobic post treatment system (activated sludge bulking; excessive growth of phototrophs) |  |

In the absence of sulphate, organic matter will be converted to methane, but in the presence of sulphate there will be a competition between the bacteria producing methane and the ones reducing sulphate, leading to H2S in the water and the biogas. Examples of factors influencing the competition are the type of bacteria, concentrations of sulphate and sulphide, pH (determines the form in which sulphide is present) and temperature. Sulphide toxicity may be severe, and can even lead to a complete process failure. When designing an anaerobic treatment system for wastewater containing high sulphate concentrations, it should be taken into account that measures will have to be taken. Wastewaters with a COD/SO42- ratio of higher than 10 can normally be treated without problems (Hulshoff Pol et al., 1998b).

##### Cations

Sodium

Anaerobic bacteria can be inhibited by cations present in the wastewater. For Na+, numbers between 6 and 40 g/l have been found as 50% inhibition values (Hulshoff Pol et al., 1998b). The large differences between values found in literature can be explained by a number of factors, such as adaptation of the biomass to higher concentrations and effects of the presence of other cations (Feijoo et al., 1995).

Calcium

Sodium toxicity is a direct toxic effect. Indirect effects can occur in the presence of Ca2+, due to the formation of precipitates (CaCO3, Ca3(PO4)2) that influence the functioning of the reactor. Carbonate ions are produced during the conversion of organic matter to methane and carbon dioxide, and these ions can precipitate with calcium ions. A Ca2+ concentration of 400 mg/l can be sufficient to cause adverse effects. Examples are scaling of biomass and clogging of pipes. Scaling of the sludge granules has a negative effect on the activity of the biomass. Operational problems can be caused when there is so much scaling that this leads to cementation of the sludge bed (Batstone et al. 2002, van Langerak et al. 2000, Hulshoff Pol et al. 1998b)

### Overview of data on anaerobic treatment of textile wastewater

In Table 2 literature data on the anaerobic treatment of different textile wastewaters are presented. References are listed below the table.

Table 2: Literature data on anaerobic textile wastewater treatment. (COD = Chemical Oxygen Demand, HRT = Hydraulic Retention Time, UASB = Upflow Anaerobic Sludge Bed reactor, UAF = Upflow Anaerobic Filter, AEBR = Anaerobic Expanded Bed Reactor, ABR = Anaerobic Baffled Reactor, 2P-APBR = Two-Phase Anaerobic Packed Bed Reactor, ITAD = Inclined Tubular Anaerobic Digester)

| Ref. | Reactor type | Wastewater type | COD | COD load | HRT | Colour / Grease # | COD | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | (g/l) | (kg/ m3.d) | (d) | (% removal) | (% removal) |  |
| 1 | Anaerobic digester | Wool scouring | - | 9.9 | - | > 47 # | >56 | - |
|  |  |  | - | 12 | - | 70 # | 70 | + enzymatic pretreatment |
| 2 | acidific. tank + UASB | black reactive dyebath | 2.25 | – | 12h | 67-71 | 74-90 | Pilot scale, Co-substrate is starch, results depend on concentration |
|  |  | red reactive dyebath | 2.70 | - | 12h | 39-58 | 27-45 |  |
|  |  | blue reactive dyebath | 1.65 | - | 12h | 48-56 | 13-84 |  |
| 3 | Lab scale UAF | Cotton desizing & scouring | 3-7 | 2.75 | - | - | 60–90 | 2.75 is maximum used |
|  | AEBR | Cotton dyeing & finishing | 0.6–1.2 | 0.63 | - | - | 50–87 |  |
|  | UAF |  | 0.6–1.2 | 1 | - | - | 50–90 |  |
|  | digester | Wool scouring | 30.5 | - | 2.4 | - | 86 |  |
|  | bioflocc. & settling |  | - | - | 4-10 | 70-90 # | 60-86 | gravity settling |
| 4 | ABR - 57 litres | Wool scouring | 28–37 | 3-5 | 7-10 | 50-65 # | 40-55 | raw wastewater |
|  |  |  |  |  |  | - | 45-60 | centrifuged wastewater |
|  | ABR - 300 litres |  | 40–97 | 3-10 | 5-9 | - | 45-18 | raw wastewater |
|  |  |  |  |  |  |  | 47-72 | centrifuged wastewater |
| 5 | 2P-APBR | Simulated dyeing water | 1.5 | 0.6-1.7 | 1 | - | 35 | Dyes: BY28, BY21, BR18, BR16, BR46, BB16, BB41 |
|  | UAF |  | 1.2–5 | 0.6-1.8 | 3-5 | 74-90 | 23-35 |  |
| 6 | UAF | Print paste thickener mix | - | - | - | - | 30-35 | - |
| 7 | Lab-scale semicontinuous | Simulated dyeing water | 1.3–2.1 | 0.13-0.2 | - | 95 | 85 | Dye: Acid Orange 7 |
|  |  |  | 1–2.1 | 0.1-0.21 | - | 100 | 85 | Dye: Reactive Black 8 |
| 8 | ITAD | Simulated dyeing water | 3.48 | 1.24 | 2.8 | 63 | 37 | Dye: Procion Red H-E7B |
|  | UASB |  | 3.48 | 1.74 | 2 | 79 | 32 |  |
| 9 | Lab-scale UASB + aerobic phase | Simulated dyeing water | 2.29–3.9 | 3.9 | 1d-16h | 88 | 77 | Procion Red H-E7B & starch |
| 10 | Digester | Size (PVA+starch) | 138.5 | - | - | - | 89 | - |
| 11 | ﬂuidised bed | Real cotton wastewater | 1.1 | 1 | 1 | 37 | 68 | - |
| 12 | Seq. lab-scale UASB/CSTR | Simulated dyeing water | - | 5-23 | - | 97-89 | 60-35 | Depending on loading rate |
| 13 | Lab-scale UASB with AS polishing | Mixed factory effluent | - | - | 8 | 96 | 90 | Most colour + COD removed anaerobically |
|  | Rotating contactors anaer. then aerobic | Polyester/cotton dyeing | - | 2-3 | 5-7h | 72 | 78 | - |

References: 1) Cail et al. 1986, 2) Chinwetkitvanich et al. 2000, 3) Delée et al 1998, 4) Gutierrez et al. 1999, 5) Mahdavi Talarposhti et al. 2001, 6) Malpei et al. 1998, 7) Manu et al. 2002, 8) O'Neill et al. 1999, 9) O'Neill et al. 2000, 10) Sacks et al. 1999, 11) Sen et al. 2003, 12) Sponza and Işic 2002, 13) Vandevivere et al 1998.

### Anaerobic decolourisation of dyeing wastewater

Anaerobic bacteria are capable of decolourising textile dyes, mainly azo dyes. Decolourisation is only the disappearance of colour, not mineralisation of the dye molecule. In quantity, the most important dye class is the one of azo dyes. Anthraquinone dyes are the second important group. In this report, only for these two dye classes the degradation mechanisms will be discussed further. It is much easier to find publications on azo dyes than on anthraquinone dyes. To compensate for the relative lack of information, this report will be a bit more extensive on the latter.

Many decolourisation studies have been conducted with single dyes. Table 3 gives an overview of literature data on the decolourisation of various kinds of dyes, sorted by dye type.

Table 3: Obtained decolourisation for different dye types. Letter after reference number refers to comments below table

| SI Name | Structure | Removal (%) | Concentration (mg/l, mmol/l #) | Retention time (d) | T (C) | Reference | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Acid Blue 25 | anthraquinone | 67 | 100 | 42 | 35 | Brown 1983 |  |
| Acid Blue 80 | anthraquinone | 7 | 100 | 42 | 35 | Brown 1983 |  |
| Acid Blue 113 | diazo | 94 | 100 | 42 | 35 | Brown 1983 |  |
| Acid Orange 3 | nitro | 62 | 100 | 42 | 35 | Brown 1983 |  |
| Acid Orange 7 | mono azo | 90 | 5 | 1 | 25 | Seshadri 1994 |  |
| Acid Orange 7 | mono azo | 99 | 100-300 | - | 30 | vdZee 2002 |  |
| Acid Orange 7 | mono azo | 98 | 100 | 10 | 24-28 | Manu 2002 |  |
| Acid Orange 8 | azo | 98 | 5 | 0.5 | 25 | Seshadri 1994 |  |
| Acid Orange 10 | azo | 81 | 5 | 12 h | 25 | Seshadri 1994 |  |
| Acid Red 14 | azo | 86 | 5 | 1 | 25 | Seshadri 1994 |  |
| Acid Red 27 | azo | 37 | 0.5 # | 3 | 30 | Haug 1991 |  |
| Acid Red 42 | azo | 62 | 80 | 16 h | - | Goncalves 1993 |  |
| Acid Red 114 | diazo | 62 | 100 | 42 | 35 | Brown 1983 |  |
| Acid Red 266 | mono azo | 95 | 100-300 | - | 30 | vdZee 2002 |  |
| Acid Yellow 17 | azo | 20 | 40 | 8-20 h | - | An 1996 |  |
| Acid Yellow 21 | azo | 98 | 0.5 # | 3 | 30 | Haug 1991 |  |
| Acid Yellow 23 | azo | 6 | 0.5 # | 3 | 30 | Haug 1991 |  |
| Acid Yellow 137 | azo | 95 | 100-300 | - | 30 | vdZee 2002 |  |
| Acid Yellow 151 | mono azo | 88 | 100 | 42 | 35 | Brown 1983 |  |
| Acid Yellow 159 | azo | 97 | 100-300 | - | 30 | vdZee 2002 |  |
| Basic Blue 3 | oxazine | 62 | 100 | 42 | 35 | Brown 1983 |  |
| Basic Blue 3 | phenoxazine | 72 | 40 | 8-20 h | - | An 1996 |  |
| Basic Blue 22 | anthraquinone | 62 | 100 | 42 | 35 | Brown 1983 |  |
| Basic Red 2 | acridine | 78 | 40 | 8-20 h | - | An 1996 |  |
| Basic Red 18 | mono azo | 92 | 100 | 42 | 35 | Brown 1983 |  |
| Basic Red 23 | azo | 99 | 100-300 | - | 30 | vdZee 2002 |  |
| Basic Violet 7 | methine | 0 | 300-2400 | 3 | - | Malpei 1998 |  |
| Basic Yellow 28 | methine | 35 | 100 | 42 | 35 | Brown 1983 |  |
| Direct Black 19 | polyazo | 51 | 100 | 42 | 35 | Brown 1983 |  |
| Direct Black 19 | polyazo | 99 | 100-300 | - | 30 | vdZee 2002 | A |
| Direct Black 22 | polyazo | 61 | 1003 | 42 | 35 | Brown 1983 |  |
| Direct Black 22 | polyazo | 99 | 100-3003 | - | 30 | vdZee 2002 | A |
| Direct Blue 15 | diazo | 83 | 1003 | 42 | 35 | Brown 1983 |  |
| Direct Blue 53 | diazo | 99 | 100-3003 | - | 30 | vdZee 2002 |  |
| Direct Blue 71 | tri azo | 100 | 100-3003 | - | 30 | vdZee 2002 |  |
| Direct Red 7 | diazo | 92 | 1003 | 42 | 35 | Brown 1983 |  |
| Direct Red 79 | diazo | 97 | 100-3003 | - | 30 | vdZee 2002 |  |
| Direct Red 80 | azo | 81 | 403 | 16 h | - | Goncalves 1993 |  |
| Direct Red 81 | diazo | 99 | 100-3003 | - | 30 | vdZee 2002 |  |
| Direct Yellow 4 | diazo | 95 | 100-3003 | - | 30 | vdZee 2002 |  |
| Direct Yellow 11 | stilbene | 53 | 1003 | 42 | 35 | Brown 1983 |  |
| Direct Yellow 12 | diazo | 75 | 1003 | 42 | 35 | Brown 1983 |  |
| Direct Yellow 12 | diazo | 86 | 100-3003 | - | 30 | vdZee 2002 |  |
| Direct Yellow 50 | diazo | 99 | 100-3003 | - | 30 | vdZee 2002 |  |
| Disperse Blue 56 | anthraquinone | 0 | 303 | 16 h | - | Goncalves 1993 |  |
| Disperse Blue 79 | azo | 100 | 1143 | 3 | 35 | Cruz 2000 |  |
| Disperse Red 106 | mono azo | 95 | 250 | 4 | - | Malpei 1998 |  |
| Disperse Red 106 | mono azo | 78 | 500 | 4 | - | Malpei 1998 |  |
| Disperse Red 106 | mono azo | 20 | 750 | 4 | - | Malpei 1998 |  |
| Disperse Red 106 | mono azo | 0 | 1500 | 4 | - | Malpei 1998 |  |
| Disperse Red 159 | anthraquinone | 0 | 300-24003 | 3 | - | Malpei 1998 |  |
| Mordant Black | mono azo | 77 | 1003 | 42 | 35 | Brown 1983 |  |
| Mordant Blue 13 | mono azo | 83 | 1003 | 42 | 35 | Brown 1983 |  |
| Mordant Orange 1 | mono azo | 95 | 1003 | 8 h | 30 | Donlon 1997 |  |
| Mordant Orange 1 | mono azo | >99 | 1003 | 8 h | 30 | Razo-Flores 1997 |  |
| Mordant Orange 1 | mono azo | 97 | 100-3003 | - | 30 | vdZee 2002 |  |
| Mordant Yellow 3 | azo | 51 | 0.5 # | 3 | 30 | Haug 1991 |  |
| Mordant Yellow 10 | mono azo | 95 | 100-3003 | - | 30 | vdZee 2002 |  |
| Reactive Black 5 | diazo | 81 | 1003 | 42 | 35 | Brown 1983 |  |
| Reactive Black 5 | diazo | 80-85 | 1003 | 4.5 h | 52 | Carliell 1994 |  |
| Reactive Black 5 | diazo | 99 | 100-3003 | - | 30 | vdZee 2002 |  |
| Reactive Black 5 | diazo | 87 | 9003 | 6.1 | 35 | Beydilli 1998 | B |
| Reactive Black 5 | diazo | 62 | 203 | 18 h | 30 | Luangdilok 2000 |  |
| Reactive Black 5 | diazo | 60 | 1003 | 18 h | 30 | Luangdilok 2000 |  |
| Reactive Black 8 | azo | 100 | 1003 | 10 | 24-28 | Manu 2002 |  |
| Reactive Black 39 | azo | 70-75 | 1:1000 | 5.5 h | 52 | Carliell 1994 | C |
| Reactive Blue 198 | oxazine | 44 | 203 | 18 h | 30 | Luangdilok 2000 |  |
| Reactive Blue 198 | oxazine | 8 | 1003 | 18 h | 30 | Luangdilok 2000 |  |
| Reactive Blue 19 | anthraquinone | 70 | 1003 | 42 | 35 | Brown 1983 |  |
| Reactive Blue 19 | anthraquinone | 57 | 203 | 18 h | 30 | Luangdilok 2000 |  |
| Reactive Blue 19 | anthraquinone | 32 | 1003 | 18 h | 30 | Luangdilok 2000 |  |
| Reactive Blue 19 | anthraquinone | 93 | 3003 | 15 | 35 | Fontenot 2003 |  |
| Reactive Blue 21 | phtalocyanine | 36 | 1003 | 42 | 35 | Brown 1983 |  |
| Reactive Blue 21 | phtalocyanine | 85-90 | 1003 | 4.5 h | 52 | Carliell 1994 |  |
| Reactive Blue 21 | phtalocyanine | 80 | 3003 | 15 | 35 | Fontenot 2003 |  |
| Reactive Blue 38 | phtalocyanine | 40 | 1003 | 4.5 h | 52 | Carliell 1994 |  |
| Reactive Blue 49 | anthraquinone | 7-10 | 1:1000 | 2 h | 52 | Carliell 1994 | C |
| Reactive Blue 72 | phtalocyanine | 25-30 | 1:1000 | 2.1 | 52 | Carliell 1994 | C |
| Reactive Blue 5 | anthraquinone | 68 | 203 | 18 h | 30 | Luangdilok 2000 |  |
| Reactive Blue 5 | anthraquinone | 37 | 1003 | 18 h | 30 | Luangdilok 2000 |  |
| Reactive Blue 220 | azo | 90-95 | 1003 | 1 h | 52 | Carliell 1994 |  |
| Reactive Brown 11 | azo | 90 | 1:1000 | 1 | 52 | Carliell 1994 | C |
| Reactive Orange 12 | azo | 90-95 | 1:1000 | 1 | 52 | Carliell 1994 | C |
| Reactive Orange 13 | azo | 85-90 | 1:1000 | 2.1 | 52 | Carliell 1994 | C |
| Reactive Orange 14 | mono azo | 98 | 100-3003 | - | 30 | vdZee 2002 |  |
| Reactive Orange 16 | mono azo | 97 | 100-3003 | - | 30 | vdZee 2002 |  |
| Reactive Orange 16 | mono azo | 100 | 50-1503 | 2 h | 19 | Kapdan 2003 |  |
| Reactive Red 2 | mono azo | 100 | 100-3003 | - | 30 | vdZee 2002 | D |
| Reactive Red 2 | mono azo | 78 | 9003 | 6.1 | 35 | Beydilli 1998 | B |
| Reactive Red 4 | mono azo | 99 | 100-3003 | - | 31 | vdZee 2002 | D |
| Reactive Red 24 | azo | 90-97 | 1:1000 | 1.3 | 52 | Carliell 1994 | C |
| Reactive Red 120 | diazo | 94 | 9003 | 6.1 | 35 | Beydilli 1998 | B |
| Reactive Red 141 | azo | 85-89 | 1003 | 4.5 h | 52 | Carliell 1994 |  |
| Reactive Red 198a | mono azo | 95 | 3003 | 15 | 35 | Fontenot 2003 |  |
| Reactive Red 198a | azo | 85-90 | 1003 | 2 h | 52 | Carliell 1994 |  |
| Reactive Red 218 | azo | 90-95 | 1:1000 | 1.3 | 52 | Carliell 1994 | C |
| Reactive Yellow 2 | mono azo | 73 | 100-3003 | - | 30 | vdZee 2002 |  |
| Reactive Yellow 3 | mono azo | 96 | 9003 | 6.1 | 35 | Beydilli 1998 | B |
| Reactive Yellow 15 | azo | 91 | 9003 | 6.2 | 36 | Beydilli 1998 | B |
| Reactive Yellow 16 | azo | 80-90 | 1003 | 6.5 h | 52 | Carliell 1994 |  |
| Reactive Yellow 17 | mono azo | 97 | 9003 | 6.2 | 36 | Beydilli 1998 | B |
| Reactive Yellow 95 | azo | 0 | 1:1000 | - | 52 | Carliell 1994 | C |
| Black SG | metal complex | 75-80 | 1:1000 | 7.5 h | 52 | Carliell 1994 | C |
| Blue PB | metal complex | 98 | 1:1000 | 2 h | 52 | Carliell 1994 | C |
| Azodisalicylate | azo | 98.8 | 753 | 8 h | 30 | Razo-Flores 1997 |  |
| Yellow Procion P3R3 | azo | 96 | 250 | 4 | - | Malpei 1998 |  |
| Yellow Procion P3R3 | azo | 95 | 500 | 4 | - | Malpei 1998 |  |
| Yellow Procion P3R3 | azo | 86 | 750 | 4 | - | Malpei 1998 |  |
| Yellow Procion P3R3 | azo | 70 | 1500 | 4 | - | Malpei 1998 |  |
| Turquiose Cibacron | cyaninic | 0 | 300-2400 | 3 | - | Malpei 1998 |  |
| Marine P | ? | 0 | 300-2400 | 3 | - | Malpei 1998 |  |

Remark A: Dye does not dissolve well, decolourisation probably combination of reduction, absorption and precipitation

Remark B: Three feeding cycles of 3003 each

Remark C: Commercial printing dye solution, diluted 1000-fold. No exact concentration.

Remark D: Reaction products are yellow

#### Azo dyes

Reduction of azo compounds has been observed in different anaerobic systems such as anaerobic sludge and anaerobic sediments, but also in anaerobically incubated pure cultures and enrichment cultures (Field et al., 1995). In case of azo dyes, which are most extensively studied dyes for anaerobic decolourisation, decolourisation means breakage of the characteristic azo-bond. In Figure 1 an example of this breakage is given.

Figure 1: Cleavage of the azo bond in azo dye Acid Orange 7, leading to formation of the aromatic amines sulphanilic acid and 1-amino-naphtol.

Most researchers are convinced that biological azo dye reduction is an extra-cellular non-specific reaction, in which reduction equivalents generating from biological reactions are transferred to the azo dye (van der Zee et al., 2003). This non-specific reaction can be speeded up by the use of redox mediators. Mechanisms for anaerobic decolourisation of other dye types have not been studied as extensively as azo dye reduction, mainly because of the big importance of azo dyes in the textile industry. Anaerobic decolourisation of for instance anthraquinone dyes has received little attention of researchers, although it is the second most important group of dyestuffs.

The aromatic amines formed in azo-cleavage are usually not degradable anaerobically, but they can be mineralised under aerobic conditions (O’Neill et al. 2000; Delée et al. 1998; Vandevivere et al. 1998).

#### Anthraquinone dyes

Anthraquinone dyes are the second most important class of textile dyes, after azo dyes (Christie 2001, Baughman and Weber 1994). Due to the focus on azo dyes, researchers often consider simulated wastewaters containing a single azo dye. Dyebaths however, are usually made up out of three dyes: combining red, yellow and blue to obtain any desired colour.  The three dyes are not necessarily of the same structure. Anthraquinone dyes have a wide range of colour in almost the whole visible spectrum, although they are most important for violet, blue and green shades (Fontenot et al. 2002, Christie, 2001). In this way they complement azo dyes, which are more important for yellow, orange and red colours (Christie, 2001). Therefore, the combination of yellow and red azo dyestuffs with a blue anthraquinone dye is quite usual. Unlike for azo dyes, the anaerobic biotransformation of anthraquinone dyes has hardly been investigated (Fontenot et al., 2002). Due to their fused aromatic structure (see Figure 2), anthraquinone dyes are resistant to degradation (Robinson et al.,  2001). Reduction of the anthraquinone moiety leads to the colourless leucoform (see Figure 2), but the molecule basically remains intact (Hao et al., 2000).

Figure 2: Structure of anthraquinone (left) and the colourless leucoform that is formed during anthraquinone reduction (right)

A wastewater treatment optimised for colour removal based on azo dyes, will not necessarily be suitable for decolourisation of anthraquinone dyes. The few publications found on anaerobic anthraquinone dye decolourisation report all very different data on the reached decolourisation and the observed toxicity to anaerobic biomass (see Table 4).

Table 4: Summary of publications on reductive anthraquinone dye decolourisation

|  | Decolourisation | Extra information | Reference |
| --- | --- | --- | --- |
| Reactive Blue 2 | 14-24 % | single strain, decolourisation stopped after 48 h | Yu 2001 |
| Reactive Blue 2 | 77% | After 72 h, consortium | Yu 2001 |
| Reactive Blue 4 | 78% | After 27.7 days, CH4 production comparable to control | Fontenot et al, 2002 |
| Reactive Blue 5 | 68% | After 16 days. C=20 mg/l | Luangd & Pansw, 2000 |
| Reactive Blue 5 | 37% | After 16 days. C=100mg/l | Luangd & Pansw, 2000 |
| Reactive Blue 19 | 83% | After 27.7 days, CH4 production severely inhibited | Fontenot et al, 2002 |
| Reactive Blue 19 | 57%, 32% | After 16 days. C=20 mg/l and C=100 mg/l | Luangd & Pansw, 2000 |
| Reactive Blue 19 | 30-100% | Average: 70% | Brown 1983 |
| Reactive Blue 49 | 7-10% | After 2 hours | Carliell et al., 1994 |
| Acid Blue 80 | 4-16% | Average: 7% | Brown 1983 |
| Acid Blue 25 | 36-100% | Average: 67%, insoluble blue pigment formed | Brown 1983 |
| Acid Blue 25 | 100% | After 21 days. 1:1 formation of 1-amino-4-phenyl-aminoanthraquinone (blue solid) | Brown 1987 |
| Acid Green 27 | 60-84% | After 48 h. | Yu 2001 |
| Basic Blue 22 | 46-86% | Average: 62% | Brown 1983 |
| Disperse Red 159 | 0% | After 3 days. C=range 300-2400 mg/l. Rate inhibited by 60% at 300 mg/l and by >90% at 2400 mg/l | Malpei et al., 1998 |
| Disperse Blue 56 | 0% | C=30 mg/l, dye made UASB reactor collapse | Delée 1998 |

Luangdilok and Paswad (2000) reported that decolourisation of solutions of Reactive Blue 5 and Reactive Blue 19 (RB19) was only due to adsorption to the biomass, no transformation of the dyestuffs could be observed. In contrast, experiments by Fontenot and co-workers (2002) did show reductive decolourisation of Reactive Blue 4 (RB4) and RB19. At high dye concentrations of RB19, colour removal occurred although the biomass was severely inhibited. The authors concluded that maintaining reduced conditions was sufficient to achieve decolourisation. When screening dyes for anaerobic degradation, Brown and Laboureur (1983) discovered that during decolourisation of Acid Blue 25 a blue precipitate was formed. Later it was concluded that this was a decolourisation product that precipitated (Brown and Hamburger, 1987). Other investigations showed severe inhibition of bacteria, for example for Disperse Blue 56, which caused the collapse of a lab scale UASB reactor that had been decolourising other dyes successfully (Delée et al., 1998). The differences in anthraquinone dye decolourisation and toxicity are probably because of differences in molecular structure (Fontenot et al., 2002).

It is clear from Table 4 that different anthraquinone dyes display different levels of inhibition of bacteria. An explanation for the inhibitory character of anthraquinone dyes can be found looking at their application in affinity chromatography. Affinity chromatography is a method for the identification, separation and purification of macromolecules (Denizli and Pişkin, 2001). So-called ligands are used in this technique, compounds that have a special affinity for the molecule that needs to be separated. The ligands are bound with one side to a carrier material, whereas the side that mimics the molecules that in nature would bind to the macromolecule remains free. On this binding site the desired macromolecule attaches (Denizli and Pişkin, 2001). Anthraquinone dyes can be used as ligands, especially for enzymes. A dye known as “Cibacron Blue” (Reactive Blue 2) is the most used dye for affinity chromatography of enzymes and proteins, but more than 100 dyes are being used in the last few years (Alberghina et al., 2000). Enzymes are inhibited by the dyes, as the natural ligands (e.g. substrates, cofactors or binding agents) can not bind because their binding site is occupied. Anthraquinone dyes mimic the structure of natural ligands for many enzymes  (Denizli and Pişkin, 2001). The process is reversible, but for desorption of the enzymes an elutant is needed (Denizli and Pişkin, 2001). The need for an elutant indicates that the bond between enzyme and anthraquinone dye is not broken easily. Anthraquinone dye inhibition of bacterial cultures can be a result of inhibition of various enzymes, due to anthraquinone-enzyme bonds that are irreversible under the applied experimental conditions.

### Application of redox mediators

Although anaerobic treatment seems a good technique to decolourise textile wastewaters, it is often too slow to be of practical use. The addition of a redox mediator however, can speed up the process and make it interesting as a first step in the biological treatment of coloured textile wastewaters (van der Zee et al., 2003). As explained in § 1.1.1, biological azo dye reduction is a non-specific process, taking place outside the bacterial cell, involving reduced electron carriers. Electron mediators added to the medium can function as electron carriers and as such catalyse the azo reduction. During the process they are continuously reduced and oxidised, which means that a single molecule will be reused as long as it is present in the system. Redox mediators can thus be added in catalytic concentrations and still be effective. The reduction of azo dyes in presence of an electron mediator is depicted in Figure 3.

Figure 3: Mechanism of the application of a redox mediator for faster azo dye reduction. Mediator structure depicted is anthraquinone-2-sulphonate.

Many of the redox mediators are quinone-like structures. Model compounds that can be used are for instance AQDS and AQS. Based on experimental results by Dos Santos (2003) AQS was chosen as a mediator in this study.

## Introduction to membrane treatment

The know how of general treatments that constitute the state of the art of the treatments methods brought to identify in the membrane treatment the option to investigate in order to assess treatability and economical feasibility, evaluate quantity and quality of the reuse options. Operational data on several representative real effluents were needed to cover the information lack to build up the overall integrated methodology to implement Good Environmental Practices with the Best Available Techniques (IPPC Directive).

Most of the techniques briefly presented in § 1.1.2 have been successfully applied for the end-of-pipe treatment and reclamation of textile wastewaters. But often, in the prospect of an integrated pollution prevention and control, end of pipe solutions are not the best possible options. A start of pipe approach can allow significant chemicals, energy and water recovery, and a real waste and wastewater minimisation. A process-integrated wastewater treatment is required to implement start of pipe solutions and membrane technology is often the best choice. Membranes allow the removal of most residual and undegraded organics (and salts), provide a constant quality permeate and could be automatically operated and controlled. Attractive features of membranes are also low weight and space requirements without use of chemicals. The equipment is modular and can be scaled up or operated at partial capacity. Moreover they are suitable for the treatment of specific process effluents because they can treat without problems also small and intermittent water flows.

Membrane filtration has been used for recycling processes in textile industry for a long-time. Ultrafiltration has been applied in full scale plants to recover polyvinylalcohol (PVA) size and to recover caustic from mercerisation process (Porter, 1990). Indigo dyes and hot water can also be recovered by membrane filtration. Lab and pilot tests have shown that NF and RO membranes can be used with effluents of reactive dyeing of cotton, of disperse dyeing of polyester and of combined reactive/disperse dyeing of cotton-polyester mix. The permeate produced by NF can be reused for rinsing while RO allow production of permeate suitable for all the technological uses. Furthermore the reuse of hot water allows a significant energy saving (Sojka-Ledakowicz et al. 1998). Rinse water treated by NF or RO was found to have great potential for reuse irrespective of the dyeing recipe (Wenzel, 1998).

### Type of membranes

The membrane classification is based on the size of the particles separable. Reverse Osmosis (RO) provides the finest degree of separation, followed by nanofiltration (NF), ultrafiltration (UF) and microfiltration (MF) . The size of the particles separable ranges from a few Angstroms up to a few microns. The operational pressure range from 1-5 bar (MF) units to 30- 50 bar (high-pressure RO systems). When high quality of the water to be reused is required, RO and NF are the possible choices.

RO membranes have a very high molecular cut-off (~200 g/mol), rejections greater than 90% for most ionic species and produce a high quality permeate. Decolourisation and removal of auxiliary chemicals from dyehouse effluents can thus be achieved in one step. NF membranes are ion selective due to negative surface charges and have a lower molecular weight cut-off (200-1000 g/mol). Multivalent anions are retained stronger than monovalent anions. Most dyes can be separated by NF membranes but some of the auxiliary chemicals can penetrate through the membrane into the permeate.

### Materials/geometry

Various module material, configurations and membrane geometries exist which are suited to a variety of applications.

Several different polymers can be used to produce polymeric membranes, making it possible to obtain different molecular weight cut off and resistance to specific process fluids. Polysulphone and polyethersulphone are used for the full range of UF membranes. Polyvinylidene fluoride (PVDF) is often used for open UF membranes, whilst polyamide is used as the thin film membrane layer in NF and RO membranes. Cellulose acetate, the first widely used polymer, is still used in certain applications but its use is limited due to its tendency to hydrolyse in alkaline conditions.

Hostile processing environments, high levels of solvents and other process considerations may dictate the use of ceramic membranes. This technology, normally adopted for UF and MF applications, typically uses an alumina or zirconia coating that is applied to the inside surface of a ceramic support. Whilst the use of this type of membrane is sometimes the only viable proposition, the capital cost is much higher than conventional polymeric membranes. However, in most cases a longer operational lifetime can be expected.

Membranes can be configured in tubular, spiral, flat sheet or hollow fibre arrangements. Tubular membranes can be used to treat viscous liquids with high levels of suspended solids and can be chemically or mechanically cleaned.

Tubular modules are relatively insensitive to clogging and more effectively cleaned during backwash-procedures.

Spiral membranes consist of tightly packed filter material sandwiched between mesh spacers and wrapped in a small tube. The high packing density significantly increases their surface area compared with tubular membranes. Spiral membranes require careful pre-filtration to avoid blocking if suspended solids are present. However, developments in spacer designs are helping to increase the number of applications to which spirals are suited. The spacers provide the channels through which the process fluid flows as it traverses the membranes surface, and therefore have a major influence on the ability to resist blocking from solids, as well as on the pressure drop along the length of the element. Spacer developments have included increasing the channel height from about 0.7 mm to over 2 mm, and changes to the geometric form of the spacer to give smoother flow channels.

### Design and evaluation

The choice of the best membrane for the applications requires testing but some basic evaluations have to be done before starting the experimental phase. The characteristics of the process fluid have to affect the choice of the right membrane. The main parameters to be considered are: nature and quantity of suspended solids, dissolved solids, molecular weight of the material, pH and temperature.

The dyeing method affects mainly the specific water consumption and therefore the volume of water discharged: in continuous dyeing processes the specific water consumption is significantly lower than batch dyeing. The dyeing recipe, water consumption, chemical dosage (dyes, salt, etc.) and control parameters are able to affect the membranes performance determining clogging, permeate, flux reduction and other temporary or permanent damages.

The quality of permeate required is also determinant in choosing the type of membrane process.

The active membrane layer consists of relatively sensitive material and a membrane is easily damaged by unplanned incidents during plant up-sets. Consequently, a thorough testing phase is required in every single case. Bench-scale tests have to be carried out to find suitable membrane types and obtain first figures on flux performance, rejection characteristics, and fouling tendencies. Lab studies should be undertaken using both synthetic and real effluent samples. Permeate and concentrate obtained from various membrane applications have to be evaluated for reuse and post-treatment. Pilot studies should be carried out thoroughly, to acquire sufficient design data and engineering solutions for operational problems, that can affect the reliability of the process. The data collected should allow for the evaluation of full scale plant performance, of investment and operational costs. Sampling programmes in lab-scale will generally not yield enough information for full scale-up. For this reason pilot-scale experiments have to be run also at the dyehouse by drawing effluent continuously from the running process to account for any possible events.

Fouling of membranes is often a weak point of membrane systems in the treatment of textile wastewater. Dyes can produce a colloidal fouling layer, which introduces a flux decline. An important part of the bench-scale and pilot study have to focus therefore on the investigation of fouling effects at high water recoveries and on the evaluation of the frequency of backwashing cycles with a suitable cleaning solution.

Efficient and cost-effective pre-treatment of the textile wastewater characterised by an high concentration of organic matter have to be tested to control fouling and enhance flux performances.

# The effluents object of the investigations

## Characterisation of the effluents selected for anaerobic tests

Sizing

To strengthen yarn before weaving, some type of sizing such as starch, gelatine, resin or a combination of these with softening substances (oils or waxes) is often applied. So sizing effluent usually has a high organic concentration of residual sizing. For instance, a sizing process from one textile factory in Belgium used 40 kg potato starch, 1 kg solid fat with 500 litre water for one batch. The residual sizing liquid volume (100-120 litre) becomes waste.

Scouring

Scouring removes waxes and destroys vegetable residues in raw materials. Alkali chemical is used to saponify the fats on the fibres. The soap that is formed then serves to emulsify the remaining waxes and to wash away any dirt or other impurities. Waste generated from the scouring process includes sodium hydroxide, waxes, greases, surfactants, chelating agents, sodium silicate, fibrous matter, processing oil, acetic acid, and phosphates.

Bleaching

Fabrics can require bleaching or whitening to prepare them for dyeing or printing or to produce a clear white fabric. Bleaches are chemical substances that oxidise coloured compounds, removing colour. Most generated pollutants from bleaching are hypochlorite, chlorine, caustic soda, acids, hydrogen peroxide, and sodium silicate.

Dyeing

Colour can be applied to fabric at any of the four steps in its processing: Coloured fibres can be manufactured before the fibre is extruded, or dyes can be applied to fibres, to yarn, or to constructed fabrics or finished product. In these processes various dyes, auxiliaries, chemicals, soap will be ending up in the wastewater.

In the experiments conducted for this study, different dyeing wastewaters were used. They were analysed and the data are presented in Table 5. To determine values for colour, spectra were recorded on a UV/VIS spectrophotometer. For scouring of indigo dyed cotton and cotton sulphur dyeing wastewater the maximum absorbance wavelength was identified and this wavelength was used during the experiments to follow the colour removal. Latest experiments were performed with polyamide acid dyeing and cotton reactive dyeing wastewater, and it was decided to try to obtain some extra information on colour removal. During the experiments, the UV/VIS spectra were recorded and after the experiments three wavelengths were chosen that represented best the colour removal process for that specific wastewater. Graphs were made with just those three wavelengths. For both wastewater spectra of different moments in decolourisation are shown in Figure 4, with the three wavelengths indicated.

Table 5: Characteristics of wastewater streams. Values indicated with ‘*’ are from samples centrifuged for 3 minutes at 10000 rpm before analysis.

| Parameter |  | Cotton Sizing | Scouring of indigo dyed cotton | Cotton Bleaching | Cotton Sulphur Dyeing | Polyamide Acid dyeing | Cotton Reactive dyeing |
| --- | --- | --- | --- | --- | --- | --- | --- |
| pH |  | 8.3 | 5.5 | 10.5 | 4.6 | 6.6 | 9.7 |
| Colour (A) | 420 nm | - | - | - | - | - | 0.460 * |
|  | 475 nm |  |  |  |  | 1.686 * | - |
|  | 500 nm | - | - | - | - | - | 0.403 * |
|  | 585 nm |  |  |  |  | 2.421 * | - |
|  | 610 nm | - | - | - | - | - | 0.286 * |
|  | 616 nm | - | - | - | 7.5 | - | - |
|  | 620 nm |  | - |  | - | 2.394 * | - |
|  | 674 nm | - | 14.8 | - | - | - | - |
| SS | mg/l | 400 | 504 | 562 | 513 | 101 | 29 |
| COD t | mg/l | 70675 | 11574 | 13012 | 6027 | 2695 * | 365 * |
| COD particulate | mg/l | 68224 | 8437 | 11051 | 5433 |  |  |
| COD suspended solid | mg/l | 2451 | 3137 | 1961 | 594 |  |  |
| COD colloidal | mg/l | 12195 | 654 | 1307 | 566 |  |  |
| COD d | mg/l | 56029 | 7783 | 9744 | 4867 |  |  |
| BOD5 | mg/l | 2700 | 3981 | Not detected | 248 |  |  |
| BOD5/CODt | - | 0.038 | 0.344 | - | 0.041 |  |  |
| COD-VFA | mg/l | 1523 | 1520 | 241 | 4489 |  |  |
| COD-VFA/CODt | - | 0.022 | 0.13 | 0.018 | 0.745 |  |  |
| Acetate | mg/l |  |  |  |  | 250 * | 14 * |
| N-NH4+ | mg/l | 0.30 | 4.98 | 7.74 | 5.14 |  |  |
| N-NO2 | mg/l | 0.30 | 0.30 | 1.79 | 0.30 |  |  |
| N-NO3 | mg/l | 0.00 | 4.11 | 8.34 | 0.30 |  |  |
| N- total | mg/l | 0.9 | 12.50 | 25.60 | 7.50 |  |  |
| P-PO43- | mg/l | 0.82 | 3.58 | 40.20 | 4.03 |  |  |
| Cl- | mg/l | - | 250 | 390 | 1040 | - | 10000 * |
| (SO42-) | mg/l | - | 280 | 207 | 312 |  |  |
| Conductivity | S/cm |  |  |  |  | 2190 | 1023 |
| Hardness | F |  |  |  |  | 7 | 10 |
| Mn | mg/l |  |  |  |  | 0.032 | < 0.01 |
| Fe | mg/l |  |  |  |  | 0.074 | 0.061 |
| Lipids | mg/l | 1331 | - | - | - |  |  |

| Figure 4: Spectra of cotton reactive dyeing wastewater (left) and polyamide acid dyeing (right) at different stages of decolourisation. Based on these spectra three “peak” wavelengths were chosen to follow the decolourisation. |  |
| --- | --- |

## Characterisation of the effluents selected for membrane tests

Membrane treatment tests were performed on 17 different raw process effluents + 2 anaerobically pretreated. They were selected by focusing on the most important effluent streams in the textile finishing industries as resulted from the analysis of the companies involved in the project. The analysis evidenced that:

- General Facilities department accounts normally for a significant factor of water consumption but the discharged organic load is negligible;

- Preparation, dyeing and printing departments include by far the most important water consuming processes and produce the biggest fraction of organic load discharged in the wastewater.

- Finishing department: water consumptions and organic load are normally much lower with few exceptions.

Therefore the effluents tested were selected among preparation, dyeing and printing operations, both from the whole processes and from the rinsing phase only. The streams tested are characterized by high variability in the dissolved organic carbon content (DOC) as well as in colour and salinity as reported in Table 6.

Table 6: Main characteristics of the ffluents tested on membrane filtration

| Process | DOC mg l-1 | Colour Abs (cm-1) |  |  | Cond. μS cm-1 |
| --- | --- | --- | --- | --- | --- |
|  |  | 426nm | 558nm | 660nm |  |
| Polyester scouring | 481 | 0.012 | 0.004 | 0.004 | 544 |
| Polyester double scouring | 737 | 0.128 | 0.068 | 0.047 | 552 |
| Polyester scouring rinsing | 16 | 0.004 | 0.002 | 0.004 | 75 |
| Polyester disperse dyeing | 300 | 0.093 | 0.019 | 0.005 | 747 |
| Polyester disperse dyeing rins. | 16 | 0.005 | 0.001 | 0.002 | 197 |
| Polyester printed wash. | 305 | 0.092 | 0.023 | 0.011 | 1096 |
| Polyestere disperse print | 57 | 0.005 | 0.001 | 0.002 | 570 |
| Viscose direct dyeing rinsing | 1 | 0.007 | 0.001 | 0.004 | 745 |
| Viscose reactive printed wash. | 700 | 0.393 | 0.330 | 0.153 | 1223 |
| Silk polymer charge | 5699 | 0.006 | 0.005 | 0.001 | 2440 |
| Silk scouring | 840 | 0.056 | 0.024 | 0.015 | 617 |
| Silk scouring rinsing | 136 | 0.016 | 0.008 | 0.008 | 149 |
| Silk yarn reactive dyeing | 775 | 2.813 | 3.939 | 0.022 | 39800 |
| Silk acid dyeing rinsing | 33 | 0.019 | 0.022 | 0.009 | 1619 |
| Polyamide Acid dyeing | 480 | 1.402 | 1.693 | 1.567 | 830 |
| Cotton Reactive dyeing | 120 | 0.466 | 0.355 | 0.151 | 16800 |
| Cotton Bleaching line | 401 | 0.022 | 0.01 | 0.009 | 1670 |
| Cotton reactive dyeing A.P. | 41 | 0.150 | 0.049 | 0.027 | 20058 |
| Polyamide acid dyeing A.P. | 69 | 0.207 | 0.062 | 0.020 | 1407 |

A.P.= anaerobically pretreated

## Tests performed on the different effluents

According to the different characteristics of the effluents, the following treatment configurations were tested on pilot scale using spiral wound polymeric membranes: UF, NF, NF after UF pre-treatment, RO after UF pre-treatment. A complete overview of the tests performed is given in Table 7, where an “X” indicates a treatment test performed at pilot scale and an “R” indicates that the treated effluent was tested for reuse in lab scale textile processes.

Table 7: Overview of the tests performed

# Material and methods

## Anaerobic treatment

### Anaerobic sludges used in the experiments

Two granular sludges were used, for different experiments. No special selection was made for each experiment, the choice for a type of sludge depended entirely on the availability of sludge.

“Nedalco sludge”

Granular anaerobic sludge from a full-scale upflow anaerobic sludge blanket (UASB) reactor treating the effluent of an alcohol distillery plant (Nedalco, The Netherlands). The sludge was stored at 4C and washed and dried on a sieve for 15 minutes before using in experiments.

“Eerbeek sludge”

Granular anaerobic sludge from a full-scale mesophilic UASB reactor treating paper mill wastewater (Eerbeek, The Netherlands). The sludge was stored at 4C and washed and dried on a sieve for 15 minutes before using in the continuous experiments. For batch tests the sludge was first acclimated at 30ºC until reaching steady state conditions, in an expanded granular sludge bed (EGSB) reactor (5.6 l) operating at a hydraulic retention time (HRT) of about 6 hours and an organic loading rate (OLR) of 2.5 kg COD /m3.day. The substrate consisted of a mixture of glucose and volatile fatty acids (VFA) at a COD ratio of 1:3. The neutralised VFA solution contained acetate, propionate and butyrate at a COD ratio of 1:1:1.

### Batch tests

Three kinds of batch tests have been conducted. As part of the continuous treatment of sizing liquid, batch tests were performed to assess the maximum specific methanogenic activity (SMA) of the granular sludge. The second group consists of degradability tests for sizing liquid, bleaching wastewater, indigo dyed cotton scouring wastewater and sulphur dyeing wastewater. The third group of tests was conducted during the continuous treatment of acid dyeing and reactive dyeing wastewater, to gain more insight on the decolourisation process.

#### Maximum specific methanogenic activity (SMA) of the granular sludge

The SMA was determined for the seed sludge and the sludge grown in the UASB reactor during the treatment of sizing wastewater.  The activity of the seed sludge and the sludge grown in the reactor was determined by measuring the changes in biogas pressure in the bottles and changes in substrate concentration. Serum bottles with a working volume of 120 ml were used in the experiments.

A VFA solution and an acetate solution with nutrients and trace elements were used as a substrate. The VFA solution consisted of a mixture of acetate, propionate and butyrate with a of ratio acetate:propionate:butyrate of 1:1.5:1.8 based on COD concentration. An acetate solution was prepared with a concentration of approximately 2 g COD/l.

The basal medium used in the experiment contained (g/l): NH4Cl (0.28), MgSO4.7H20 (0.11), K2HPO4 (2.00), NaH2PO4 (3.33), yeast extract (0.10). Trace elements were added in an amount of 1 ml of trace element solution per litre of medium. The trace element solution contained (g/l):

H3BO3 (0.05), FeCl2.4H2O (2), ZnCl2 (0.05), MnCl2.4H2O (0.05), CuCl2.2H2O (0.03), NH4SeO3.2H2O (0.05), AlCl3.6H2O (2), NiCl.6H2O (0.05), NaSeO3.6H2O (0.1), EDTA (1), resazurin (0.2); HCl (0.001ml/l).

All experiments were performed in duplicates or triplicates (R1, R2, R3, additions were done without without changing (replacing) medium and biomass) using 1 g VSS/l in the assay. SMA of granular sludge was determined before set up of the reactor and each time when the HRT was increased. The serum bottles contained 50 ml of granular sludge (1 g VSS/l), the standard VFA or acetate with concentration of 2 g COD/l, basal medium and trace elements. Acetate or VFA standard was added from a neutralised stock solution containing 100 g COD/l. The serum bottles were closed and the gas phase was changed to N2/CO2 (70/30). 1ml/l of Na2S (1M) was added to obtain completely anaerobic conditions. The serum bottles were incubated in a temperature room at 30±2C and shaken at 50 rpm. Samples were taken 3-4 times per day for determination of VFA and pressure. In these experiments, the third successive feed was used for calculation. After termination of each feed, the concentrated standard VFA or acetate solutions were injected into the bottles using syringe and needle.

#### Anaerobic degradability tests

The basal medium used in the experiment, contained nutrients and trace elements in the concentrations described in the previous section.

The experiments were performed in 1000 or 500 ml glass serum bottles. The bottles contained 500 ml of basal medium (100 ml), Nedalco granular sludge (2 g VSS/l), and wastewater that was diluted with demineralised water to obtain the desired total COD concentration around 5200 mg COD/l for sizing, 6027 mg COD/l for dyeing, 5787 mg COD/l for scouring, and 5027 mg COD/l for bleaching. Sodium bicarbonate also was added to the mixture with a ratio of 1g NaHCO3/g non-acidified COD. The amounts of NaHCO3 added were 4.975 g per 0.5 litre for sizing, 0.8 g per 0.5 litre for dyeing, 2.9 g per 0.5 litre for scouring, and 2.45 g per 0.5 litre for bleaching wastewater. Then the serum bottles were closed with a butyl rubber septum (Rubber B.V., Hilversum, The Netherlands) and flushed with an N2/CO2 (70/30) gas mixture. To ensure completely anaerobic conditions, 1 ml/l Na2S (1M) was added to each bottle. All bottles were incubated at 30±2C on orbital-motion shaker at 50 rpm (Gerhardt, Bonn, Germany). Sludge was let to settle for 5 minutes before samples were collected for determination of pH, VFA, CODd, and CH4. Time period of the assay was about 30-32 days.

#### Effect of the initial wastewater concentration on anaerobic degradability

The experiment at different initial CODt concentrations was performed to assess the effect of the wastewater concentration on the anaerobic biodegradability rate with three of the wastewater streams: sulphur dyeing, indigo dyed cotton scouring and bleaching.

The basal medium used in the experiment had the following composition:

Nutrients (g/l):

NH4Cl (0.28), MgSO4.7H20 (0.10), CaCl2.H20 (0.075), KH2PO4 (0.25), yeast extract (0.10).

Trace elements (g/l):

H3BO3 (0.05), FeCl2.4H2O (2), ZnCl2 (0.05), MnCl2.4H2O (0.05), CuCl2.2H2O (0.03), NH4SeO3 .2H2O (0.05), AlCl3.6H2O (2), NiCl.6H2O (0.05), NaSeO3.6H2O (0.1), EDTA (1), resazurin (0.2); and HCl (0.001 ml/l).

Initial wastewater COD concentrations used, are given in Table 8. To obtain a filtered sample a 4.4 µm folded paper-filter (Schleicher & Schuell 5951/2, Germany) was used. Dilution to lower concentrations was done with demineralised water.

Table 8: Experimental set-up for the assessment of the effect of the initial wastewater concentration on degradability. All concentrations are in mg COD/l

| Experiment number | Sulphur dyeing | Scouring | Bleaching |
| --- | --- | --- | --- |
| R1 | 2223 | 3010 | 3004 |
| R2 | 4368 | 6019 | 6007 |
| R3 | 6539 (raw) | 6007 (filtered) | 8769 |
| R4 | 5885 (filtered) | 9029 | 13049 (raw) |
| R5 | - | 11575 (raw) | 11960 (filtered) |
| R6 | - | 8437 (filtered) | - |

The experiments were performed in 1000 and 500 ml glass serum bottles. The bottles contained 250 ml of basal medium (50 ml), Nedalco granular sludge (10 g VSS/l), and different wastewater concentrations as described previously (substrate). For raw wastewater, the nutrient was added in powder form directly to the serum bottles, to assure that no lack of nutrients would occur during the tests.  After addition of sodium bicarbonate, sulphuric acid was added to adjust the pH to 7±0.5. Then the serum bottles were closed with a butyl rubber septum (Rubber B.V., Hilversum, The Netherlands) and flushed with N2/CO2 (70/30). To ensure completely anaerobic conditions, 1 ml/l Na2S (1M) was added to each bottle.  All bottles were incubated at 30±2C on an orbital-motion shaker at 50rpm (Gerhardt, Bonn, Germany). Sludge was let to settle for 5 minutes before samples were collected for determination of pH, colour, VFA, CODd and CH4. All experiments were carried out in duplicates and included a blank sample. The experiment was carried out with two successive feedings until a steady state was obtained. After termination of the first feed, the supernatant liquid was removed by siphon and replaced by a fresh full second feed and the procedure was the same as for the first feed.

#### Decolourisation tests

All batch tests were conducted in 120-ml serum bottles containing 50 ml of wastewater and a N2-CO2 (70%-30%) headspace. As co-substrate either a VFA/Glucose solution or a textile size waste stream were used. The VFA/Glucose stock solution had a concentration of 150 g COD/l, the size liquid had a concentration of 60 g COD/l. For the processes and the composition of the wastewaters see chapters 3 and 4. Before use in the experiments the pH of the wastewaters was adjusted to pH=7. As a redox mediator anthraquinone-2-sulphonate (AQS) was used.

Bottles were filled with 50 ml wastewater, Eerbeek sludge in a concentration of 1.3 g VSS/l and mediator where applicable, then closed with butyl rubber stoppers and sealed with aluminium crimp caps. The gas phase was then changed to N2-CO2 and the co-substrate was added where applicable. Bottles were incubated at 30C for mesophilic experiments, and at 55C for thermophilic experiments. All bottles were shaken at 50 rpm. As the focus of the experiments is decolourisation, only colour was analysed. No nutrients were added to the wastewater.

### Reactor experiments

#### Anaerobic treatment of sizing liquid

The potential for the treatment of high strength sizing effluents in the UASB system was assessed, with changing organic loading rate (OLR), hydraulic retention time (HRT)

The experiment was performed using a lab-scale UASB reactor in a controlled temperature room (30±2C). The reactor configuration is shown in Figure 5.

The UASB had an internal diameter of 90 mm, and a total height of 300 mm. Total reactor volume was 2.1 litre. Biogas produced was lead through an alkaline liquid (10% NaOH) displacement system, to remove CO2. Methane production was measured with a gas meter (Meterfabriek Schlummbergen, Dordrecht). Raw wastewater (stored at 10C for the duration of the experiments) and buffer (NaHCO3) were mixed and fed to the reactor with a variable speed peristaltic pump (Watson Marlow, UK). Nutrient solution was pumped to the reactor using a Minipuls 3 peristaltic pump, (France). This mixture and the nutrient solutions were stored at 20± 5C (not in the refrigerator) during the operation of the reactor.

Figure 5: Scheme of lab-scale UASB reactor used for the treatment of sizing liquid.

A nutrient and trace elements solution was supplied to the influent by a neutralised stock solution with a dose of 6 ml nutrients solution and 0.1 ml trace solution for 1 litre of influent. Composition of the stock solution was as follows (g/l): NH4Cl, 0.75; MgSO4.7H2O, 15; K2HPO4, 212; NaH2PO4, 276; CaCl2.2H2O, 3; yeast extract, 5. The trace element solution contained (g/l): H3BO3 (0.05), FeCl2.4H2O (2), ZnCl2 (0.05), MnCl2.4H2O (0.05), CuCl2.2H2O (0.03), NH4SeO3 .2H2O (0.05), AlCl3.6H2O (2), NiCl.6H2O (0.05), NaSeO3.6H2O (0.1), EDTA (1), resazurin (0.2); and HCl (0.001 ml/l).

Following the Guide to anaerobic laboratory work (1999), an amount of sodium bicarbonate solution should be added to wastewater in the ratio of 1 g NaHCO3 / g COD non-acidified wastewater to prevent the pH of the influent dropping under 6.5. In this case 0.995g NaHCO3 was added per g influent COD.

Nedalco granular sludge was used in the experiment. Before running with real wastewater the granular sludge was adapted with a VFA solution that consisted of a mixture of acetate, propionate, butyrate (acetate:propionate:butyrate being 1:1.5:1.8 on a COD concentration basis), with a total COD concentration of approximately 3 g/l.

The reactor was inoculated with 315 g wet granular sludge (30 g VSS / dm3 volume of reactor) which was first dried on a sieve for 15 minutes. Concentration of volatile suspended solid (VSS) was 9.55%. The maximum specific methanogenic activity of sludge determined with VFA solution was about 1.35-1.41 g COD /g VSS.day.

Operation of experimental UASB-reactor

According to instructions of Hulshoff Pol (1998) concerning the start up of the reactor, the wastewater was diluted with tap water to obtain an influent of around 2000mg COD/l. Every day influent was prepared by diluting raw wastewater with tap water and buffering with NaHCO3 (powder). The initial hydraulic retention time (HRT) was 15 hours and the organic loading rate (OLR) was 3.2 kg COD/m3.day. The loading rate was gradually increased along with the improving COD treatment efficiency, viz. each time when a 75-85% COD reduction or higher was obtained and VFA was less than 100mg/l or pH did not drop. HRT was changed from 15, 12, 10, 8 and 6 hour, organic loading rate was increased 3.2, 4.0, 4.8, 6.0, and 8 kg COD/m3.day to assess maximum loading rate.

#### Anaerobic treatment of dyeing wastewater

The used reactors were Expanded Granular Sludge Bed type reactors, operational parameters are given in Table 9 and the reactor set-up in Figure 6.

Figure 6: Schematic reactor set-up

Table 9: Operational parameters for EGSB type reactors used in this study

|  | Acid dyeing | Reactive dyeing |
| --- | --- | --- |
| Effective volume (l) | 2 | 2 |
| Water height (m) | 0.82 | 0.82 |
| Organic Loading Rate (g/l.d) | 4 | 1 |
| Upflow velocity (m/h) | 10 | 10 |
| Influent Flow (l/d) | 3 | 5.5 |
| Hydraulic Retention Time (h) | 16.2 | 8.8 |

The reactors were inoculated with 650 g wet granular sludge ( 15.6 g VSS / dm3 volume of reactor).

Samples were taken for analysis on Colour, COD and VFA. Methane production was measured using gas meters and a NaOH carbon dioxide trap. An empty Erlenmeyer flask was connected between the reactor and the flask containing NaOH solution, to prevent accidental back flow of sodium hydroxide to the reactor.

The dye wastewater does not contain enough material that can act as a co-substrate for the biomass. As carbon source a third textile waste stream was chosen, size liquid. To give yarns strength during weaving, they are covered with a protective layer, a “size”. One of the materials that can be used as a cover is a mixture of starch and fat in water. In case of the size liquid that was used, it consists of 500 litre water, 40 kg starch and 1 kg solid fat. Of every size bath around 150 litres are discharged after the process. This waste stream is highly concentrated, with a COD of around 60 g/l. It contributes considerably to the total COD load of a factories’ effluent, so it would be an improvement if this waste stream could be separated from the rest of the wastewater and used for a treatment purpose such as anaerobic decolourisation.

### Analyses

#### COD

COD of the wastewaters was determined using the cuvette method of Dr Lange.

Sizing liquid

Raw samples were analysed for total COD (CODt), 1.0-1.6μm glassfaser rundfilter (Schleicher & Schuell GF 52, Germany) samples for particulate COD (CODp) and 0.20μm membrane filter (Schleicher & Schuell NL 16, Germany) samples for dissolved COD (CODd). Suspended solids COD (CODss), and colloidal COD were calculated as the differences between CODt and CODp and the difference between CODp and CODd respectively.

Acid dyeing wastewater

Centrifuged sample (10000 rpm for 4 minutes) was diluted 1:1 with demineralised water to assure the sample COD would be within the 100-2000 mg COD/l range of the cuvette.

Reactive dyeing wastewater

Centrifuged sample (10000 rpm for 4 minutes) was diluted 1:10 with demineralised water to assure that the chloride concentration of the sample would be below 1 g/l. A higher concentration causes precipitation of chloride with the chromate in the cuvette and this interferes with the measurement, leading to too high COD values.

#### Colour

Indigo dyed cotton scouring and black sulphur dyeing wastewaters

In order to detect maximum absorbance, samples were diluted in the ranges 2, 5, 10 and 20 times in phosphate buffer (10.86 g/l NaH2PO4.2H2O; 5.38 g/l Na2HPO4.H2O). These mixtures were measured spectrophotometrically with a UV/VIS spectrometer Lambda 12 with 200-900 nm to detect the maximum absorbance. For later analyses the samples were diluted 10 times and measured spectrophotometrically with a Spectronic 60 spectrophotometer (Milton Roy Analytical Products Division, Oostende, Belgium) at the absorbance maximum of 674 nm for indigo dyed cotton scouring wastewater and 616 nm for sulphur dyeing.

Polyamide acid dyeing and cotton reactive dyeing wastewaters

Absorption was measured in centrifuged samples (10000 rpm) at various wavelengths using a UV-VIS spectrophotometer (Perkin-Elmer Lambda 12). To determine the suitable wavelengths first a complete scan was made from 200 to 800 nm. The part between 200 and 400 nm showed a lot of distortion, and from 700 to 800 nm the spectrum was almost flat. Therefore it was decided to look only at the range of 400 to 700 nm. Decolourisation graphs can best be made for certain wavelengths. For both waters the wavelengths were chosen according to the decolourisation ‘pattern’ shown during the experiment. The chosen wavelengths will be explained for each wastewater in its respective chapter.

#### Volatile Fatty Acids (VFA)

The size solution used as co-substrate in the reactor will lead to formation of VFA. Effluent samples were analysed for VFA using a gas chromatograph. Characteristics of the GC are:

Gas Chromatograph			- 5890 A

Injector					- 6890 series (HP)

Autosampler controller			- G1512 A (HP)

Column	- 2 m x 2 mm glass column

(packed with Supelcoport 100-120 mesh, coated with 10% Flourad FC 431)

Carrier gas					- Nitrogen

Detector					- Flame Ionisation Detector

Oven temperature				- 130°C

Injector temperature			- 220°C

Detector temperature			- 240°C

Software					- Chromeleon 6.01 Build 447 (Under Windows NT)

#### Methane

During the batch experiments for anaerobic biodegradability of sizing liquid, scouring wastewater, sulphur dyeing wastewater and bleaching wastewater the accumulation of produced methane gas was measured with a Marriott displacement set up filled with 1.5 % NaOH solution (see Figure 7).

Figure 7: Marriott displacement system to measure methane

During the experiment to measure the maximum specific methanogenic activity (SMA) of the granular sludge, the pressure in the bottles was measured with a LCD (0-4 bar) pressure device.

#### SO42-, Cl-, PO4

Sulphate (SO4), chloride (Cl-), and phosphate (P-PO4) were measured by ion chromatography (Packing Chrompack Ionosphere).

#### Lipids

Total lipids were determined according to Sanders et al. (2001), the samples were acidified with concentrated HCl to pH 1 and subsequently filtered through filter paper (Schleicher & Schuell 5951/2) overlaid with suspension filter powder (1g). Filter paper and solids were fitted into a Soxhlett extraction thimble (Schleicher & Schuell, extraction thimbles 33x118mm) that was dried in an oven at 103C for 1.5h. The weighed extraction flask and add 150ml petroleum ether was connected to a Soxhlett apparatus. Lipid was extracted at a rate of 20 cycles/h for 4h (APHA, 1995). After evaporation of petroleum ether, the flask was weighed and then total lipid was calculated by the difference from the initial weight.

In order to detect maximum absorbance, samples were diluted in the ranges 2, 5, 10 and 20 times in phosphate buffer (10.86g/l-NaH2PO4.2H2O; 5.38g/l- Na2HPO4.H2O). These mixtures were measured spectrophotometrically with a UV/VIS spectrometer Lambda 12 with 200-900nm to detect the maximum absorbance. Then colour was diluted 10 times and measured spectrophotometrically with a Spectronic 60 spectrophotometer (Milton Roy Analytical Products Division, Oostende, Belgium) at absorbance maximum of 674nm for scouring and 616nm for dyeing.

#### Respirometry

Respirometry was used to assess changes in the aerobic biodegradability of the wastewater after treatment. Figure 8 shows a schematic set-up of a respirometer.

| Figure 8: Respirometer (schematic) | Figure 9: used RA1000 respirometer |
| --- | --- |

The aeration vessel (1) maintains the experimental conditions constant. Aeration, pH and temperature are controlled. The respiration chamber (2) is where the oxygen concentrations are measured. Because of the valves (3) only one oxygen probe (4) needs to be used: the valves cause the flow to intermittently pass the electrode on the way in and the way out of the respiration chamber. With those oxygen concentrations the respiration rate is calculated. Figure 9 is a photo of the respirometer used in the experiments, a RA1000 type. For more information on respirometry see TOWEF0 deliverable 10.

Sludge was collected at the municipal treatment plant of the village Bennekom. It was sieved before use. Experimental conditions of the respirometric tests were: Volume respiration chamber = 0.728 litre, sludge volume = 1.75 litre, pump flow = 16 l/h, T = 20C, pH = 7.

## Membrane treatment

### The experimental equipment

#### SDI

The choice of the right membrane for the full scale application requires testing but some basic evaluations have to be done before starting the experimental phase, based on the characteristics of the effluent to be treated and on the quality of permeate required. The main parameters to be considered are the ones determined during the preliminary characterisation. In particular for RO and NF processes, the SDI is a very significant parameter.

Silt Density Index is measured with an automatic instrument AutoSDI (Automated SDI Tester) by Osmonics Inc.

SDI value is related to the decreasing of flow rate during 15 minutes filtration through a 0.45 mm filter. During the test, a constant pressure of 30 psi (2,07 bar) is applied on the feed. The time required to collect 500 ml of filtered flow is registered at the beginning (t0’) and after 5, 10 and 15 min filtration. If the time for filling the first 500 ml is superior than 3 min, the test is automatically stopped resulting in the clogging of the filter.

Formula used for the SDI calculation are:

SDI5 = [1 – ( t0’ / t5’ )] . 100/5

SDI10 = [1 – ( t0’ / t10’ )] . 100/10

SDI15 = [1 – ( t0’ / t15’ )] . 100/15

Where t0’ indicates the time (in sec) required to fulfil 500 ml at the beginning of the test; t5’ is the time required to fulfil 500 ml after 5 min filtration, the same for t10’ after 10 min filtration and t15’ after 15 min.

Maximum value of these indexes are:

SDI5 max = 20 ;               SDI10 max = 10;               SDI15 max  = 6,7.

The index usually reported as SDI is SDI15, which gives a response on the kind of membrane to be properly used (UF, NF, OI). Values superior to 6 indicate that NF and OI are not possible without a pre-treatment. Nevertheless, experimental trials of direct NF were carried out without clogging the membrane even if the SDI test suggested a different behaviour (time for filling 500 ml at the beginning of the test was superior than 3 min).

#### Bench scale plant

Trials on laboratory scale have been carried out on the SEPA CF Membrane Cell, by Osmonics Inc. (see picture in Figure 10)

SEPA CF is a bench-scale membrane system that mimics the operating crossflow conditions of a spiral wound membrane element. The membrane system uses a flat sheet membrane cell with an effective membrane surface area (dimension of the sheet 190x140 mm),with feed and permeate spacers and tangential feed flow as in spiral wound systems. The cell is held closed pneumatically by a piston clamping mechanism and can provide pressures up to 6.9 bar. For security reasons, the internal preassure cannot overcome the pressure provided on the cell.

Membranes for RO, NF, UF and MF can be tested on the SEPA CF.

The feed solution is pumped within the lower part of the cell where it flows tangentially to the membrane surface. The permeate flow crossing the membrane is collected toward the centre of the upper part of the cell through a permeate carrier. The concentrate flow is collected in the lower part of the cell where a valve regulate the circulation of the concentrate and a manometer indicates the operational pressure.

Figure 10: Picture of the bench scale test equipment SEPA CF

On several membrane sheets allocated in the bench scale system, two kind of trials have been carried out:

- Characterization of the membrane with deionised water

- Complete recirculation test, using real effluents

In this way, a preliminary evaluation on the affinity existing in the combination of a specific effluent and a membrane type is possible observing the decreasing of flow rate passing from pure water to real effluent and the quality of the permeate, as described below (see description of experimental activities § 3.2.3.1. and results in chapter 4). The bench scale SEPA is therefore used to select the proper membrane to be used in the further pilot scale investigation. Anyway, the flux values obtained, even if good for comparison among various membranes, are not reliable for pilot scale/ full scale fluxes estimation. In fact, important differences between bench and pilot scale were observed while the quality of the permeate obtained on bench scale were normally in accordance with the values obtained from the pilot run.

#### Pilot scale plant

The pilot scale plant MEMBRATEST by Osmonics Inc. allows for the evaluation of tangential MF UF NF and RO, implementing the same fluidodynamics of the full scale plants.

The plant is composed of:

- 50 l tank to stock the feed (it can be used also in washing operations)

- pre-filter made of polypropylene fiber (length: 24.8 cm; pore diameter: 5 -20 mm);

- centrifugal feeding pump up to 5 bar;

- additional pump up to 20 bar;

- a vessel to install a spiral wounded polimeric membrane (diameter 4,6 cm, length 30,5 cm, membrane surface 0,3-0,4 m2);

- a vessel to install a ceramic tubular membrane (not used);

- flow control valves, manometers and flowmeters.

The plant is made of stainless steel AISI316L with the exception of flow meters and permeate and concentrate pipes which are in plastic material resistant to high temperatures and acid/basic conditions (see picture in Figure 11).

In order to control the temperature from growing, due to the pressure applied and the attrition during the filtering, the concentrate recirculation pipeline passes through a 200 l tank filled with water. In this way it is avoided to reach temperature as high as 50 °C which can damage the membrane, and a more gradual temperature change is guarantee (growing 1°C every 15’).

Figure 11: Picture of the pilot scale plant

On the pilot plant, the trials carried out, beside the characterization with deionised water and the complete recirculation test with real effluents (as described for the bench scale system) are:

- Concentration effect test with real effluent

- Second characterization with deionised water.

These trials allow for an evaluation of the effect on the permeate quality of growing concentration of the feed as for the operative conditions of a full scale plant. By the second characterization it is possible to evaluate fouling phenomena on the surfaces and the relative cleaning requirements (see description of experimental activities § 3.2.3.2. and results in chapter 4).

#### Membranes

The membrane moules selected for the experimental activity are polymeric spiral wounded produced by Osmonics Inc., surface 0,35 m2.

In the following Table 10, Table 11, Table 12 all the characteristics of the membrane used are reported, as given by the producer:

Table 10: Characteristics of UF membranes

| Membrane: | MW | PW | GH | GK | ER |
| --- | --- | --- | --- | --- | --- |
| Type | UF | UF | UF | UF | UF |
| Material | polyacrilonitrile mod. | polyether sulphone | thin film processo | thin film processo | poly-sulphone |
| p op. | 2.1 bar | 2.1 bar | 10.3 bar | 4.8 bar | 3.4 bar |
| p max |  |  |  |  |  |
| T max |  | 50°C | 50°C | 50°C |  |
| pH range |  | 2-11 | 1-11 | 2-11 |  |
| Rejection or MWCO | 50000-100000 D | 12000 D | 1000 D | 2000 D | 15000-30000 D |
| Permeability | >600 l/(h*m2) | 500 l/(h*m2) | 10 l/(h*m2) | 20 l/(h*m2) | 350-525 l/(h*m2) |

Table 11: Characteristics of NF membranes

| Membrane: | DK | DL | CK | HL |
| --- | --- | --- | --- | --- |
| Type | NF | NF | NF | NF |
| Material | thin film processo | thin film processo | cellulose acetate | thin film standard |
| p op. | 6.9 bar | 6.9 bar | 6.9 bar | 6.9 bar |
| p max | 41.37 bar | 41.37 bar |  | 41.37 bar |
| T max | 50°C | 50°C |  | 50°C |
| pH range | 2-11 | 2-12 |  | 1-10 |
| Rejection or MWCO | 98% MgSO4 | 98% MgSO4 | 60-75 % NaCl | 98% MgSO4 |
| Permeability | 26 l/(h*m2) | 44 l/(h*m2) | 17-26 l/(h*m2) | 44 l/(h*m2) |

Table 12: Characteristics of RO membranes

| Membrane: | AD | AE | AG | AK | SC | SE | SG |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Type | RO | RO | RO | RO | RO | RO | RO |
| Material | thin film poly-ammide standard | thin film poly-ammide standard | thin film poly-ammide standard | thin film poly-ammide standard | S thin film poly-ammide processo | S thin film poly-ammide processo | S thin film poly-ammide processo |
| P op. | 55 bar | 55 bar | 13.8 bar | 6.9 bar | 55 bar | 27.6 bar | 13.8 bar |
| P max | 82.74 bar | 82.74 bar | 41.37 bar | 41.37 bar | 82.76 bar | 41.37 bar | 41.37 bar |
| T max | 50°C | 50°C | 50°C | 50°C | 50°C | 50°C | 50°C |
| pH range | 4-11 | 4-11 | 4-11 | 4-11 | 2-11 | 4-11 | 2-11 |
| Rejection or MWCO | 99.5 % NaCl | 99.2% NaCl | 99.5% NaCl | 99% NaCl | 99.5% NaCl | 99% NaCl | 98% NaCl |
| Permeability | 6 l/(h*m2) | 10 l/(h*m2) | 21 l/(h*m2) | 38 l/(h*m2) | 5 l/(h*m2) | 7 l/(h*m2) | 14 l/(h*m2) |

### Analytical characterization

For the characterization of raw effluents, permeates and concentrates produced by membrane filtrationstandard methods have been applied according to the procedures I.R.S.A. – C.N.R. (C.N.R., 1994) and Standards Methods (A.P.H.A., 1989).

Sampling methods are described in the following, depending on the experimental trial.

#### TOC

The measurements are made through a TOC analyser, PC-supported, “TOC-VCPH/CPN – SHIMADZU”. The sample undergoes a catalysed combustion at 680 °C and the gaseous emissions pass an infrared analyser which measures the quantity of the produced CO2, as absorbance of infrared rays. A varying electrical potential shows the energetic gap produced by this absorbance; integrating and calibrating the curve representing the signal, the analyser gives a measure of the Total Organic Carbon present in the sample, as an average value of three measurements on the same sample.

The superior limit of the measure range is 2000 mg l-1; over this value a dilution is required which can be activated with an instrument’s function of self dilution with pure water.

As the procedure of sampling always requires a pre-filtration step (0,45 mm) before analysing the samples, the value of TOC coincides with the Dissolved Organic Carbon (DOC) since all the compounds are in a dissolved form. Organic content can be represented both with TOC and with DOC. Pure water is used before and after each measurement series to assure the cleaning of the surfaces. Beside the TOC, the analyser gives a measure of TC (total carbon) and IC (inorganic carbon) as well.

#### SST

The Standards Methods procedure is used, with a filter of 1.1 mm porosity. The method resulted not very reliable for values inferior to 5 mg/L therefore the SST in the membrane permeate is never reported. The values in feed and concentrate are always reported but, below the threshold value, they have to be considered only as reference values.

#### Conductivity

The instrument is a termistore conductivity-meter, commercial name LF 197/LF 197-S – WTW, which automatically gives a normalised value of conductivity at the temperature of 20 °C, through a non-linear function, standardized by the German norms DIN.

#### Temperature

A laboratory Hg thermometer is used.

#### pH

A glass electrode pH-meter, Model SA 520, is used.

#### Turbidity

A laboratory instrument RATIO TURBIDIMETER HACH MODEL 18900 is used. The superior limit of its validity range is 200 NTU.

#### Colour

Colour is measured in terms of absorbance on an optical path of 1 cm, on 0.45 mm filtered samples, at three (426, 558, 660 nm) or six (426, 558, 660, 436, 525, 620 nm) wave lengths commonly used to characterise textile effluents. Colour is proportionally growing with absorbance. The spectrophotometer used is “UV-Vis Unicam Spectrophotometer Helios-α – Thermospectronics”.

### Experimental activities

#### Selection of membranes on bench scale tests

##### Characterization -BS

Membrane characterization consists of circulation of deionised water fed to the equipment in order to evaluate the maximum flow rate and eventual loss of flow rate due to fouling on the membrane surfaces.

Comparing the fluxes obtained with pure water and with the real effluent in subsequent tests, affinity between membrane and effluents emerges as the grade of reduction of flow rate passing from water to real effluent filtration. After cleaning the membrane a new characterization is normally carried out in order to evaluate the recovery of permeability.

Membrane sheets are tested with constant pressure (depending on the membrane type, up to 6.9 bar), feeding the apparatus with a 4 -5 l tank of deionised water and recirculating continuously both permeate and concentrate flows produced.

Bench scale characterization is not possibile for RO membranes.

For each BS characterization carried out on the various effluents, the table of flow rates determined at varying temperatures for each membrane tested, usually at one fixed pressure, is reported for each effluent tested (chapter 4).

##### Complete recirculation test –BS

It consists of a filtration with real effluent, whose permeate and concentrate are continuously recycled in the feeding tank for 1 hour, without discharging the permeate produced, assuring an almost constant concentration of the feed.

Operational pressure is fixed according to the type of membrane (up to 6.9 bar).

Samples are taken at the beginning and at the end of the trial (250 ml) to compare the quality of the permeate.

Evaluating the loss of flow rate and the quality of the permeate after 1 hour filtration at constant conditions, it is possible to assess if fouling occurs on the surface due to the inter-actions between effluent and membrane emerging with the passing of filtration time, as the feeding quality can be considered constant.

All the membrane showing a good behaviour during the characterization have been submitted to the complete recirculation test. The membrane cell is fed with 3 l effluent and sample of 50 ml are collected.

The run is represented by two tables:

- flow rate with real effluent at constant feed concentration and relative decrease in flow rate in reference to the value with pure water;

- quality of the permeate sampled after 5’ or 15’ filtration.

##### Choice of the membrane

Only the membranes selected by giving better performances (in terms of fluxes and quality of permeates) on complete recirculation test on bench scale have been tested on pilot scale.

#### Pilot scale run

##### Characterization -PS

Passing from the bench scale to the pilot plant, only the membrane selected by giving better performances on lab scale has been characterized on pilot scale with a tubular spiral wound geometry, as described in the experimental equipment (§ 3.2.2.3).

Characterization on pilot scale is performed by filtrating and continuously recirculating 25 –27 l deionised water (from the feed tank) and recirculating the concentrate at 250 l·h-1 flow rate.

The cooling step through the water tank (§ 3.2.2.3) is by-passed during the characterization. In this way, the temperature is free to grow (due to the pumping and attrition on the membrane surface) and its effect on the filtration is monitored

Characterization is performed at different pressure conditions depending on the filtration type:

- UF (1,4 bar; 1,9 bar; 2,3 bar; 2,8 bar)

- NF (6 bar; 6,9 bar; 9 bar)

- RO (6 bar; 10 bar; 13.8 bar)

During the sampling (250 ml) the flow rate is evaluated measuring the time required to fulfil a given volume.

It is possible to evaluate: maximum flow rate obtainable; variation of flow rate with pressure at a given temperature or vice versa; presence of fouling phenomena on the surface.

As for the BS characterization, the pilot scale characterization is represented by a table of flow rates determined at varying temperatures for each membrane tested, for the pressure values in the range.

##### Complete recirculation test -PS

The test is described above (§ 3.2.3.1.2) for the bench scale system; the feed tank is fulfilled with at least 27 l of real effluent. The concentrate recirculation flow rate is fixed at 250 l·h-1.

Measurements of flow rate and temperature are taken every 15’ –20’.

It is possibile to evaluate eventual interactions occurring between membrane and effluent with time.

The results are presented in the tables:

- flow rates at varying temperature at fixed time intervals (mostly 0’, 15’, 30’, 45’, 60’);

- quality of the permeate at the beginning and at the end of the run (or an average of both values).

##### Concentration effect test -PS

The same volume completely recycled in the previous run is used as initial feed for the complete recirculation test; the concentrate recirculation flow rate stays 250 l·h-1.

In the concentration effect test, the concentrate is continuously recirculated in the feeding tank (real effluent) while the permeate is discharged. These conditions bring to a growing concentration in the feeding tank with the time, while reducing the initial feed volume up to the 80%. Starting with a feed volume of 25 l, four discharges of 5 l are carried out implying 20% increase in concentration each.

The membrane is therefore used in conditions more similar to those applied in a full scale plant where the produced permeate is continuously diverted and the concentration of the influent can vary and easily grow.

The concentration effect is monitored with the permeate flow rate and quality. Evaluation on the concentration growing limit not compromising the permeate quality , are possible.

Samples are taken at known level of concentration (known quantity of permeate discharged and consequently feed volume reduction, 20, 40, 60, 80 %) in order to evaluate the quality through an analytical campaign. Measurement of flow rate and temperature are also taken. Where the feed volume was not enough, samples have been collected only at three intervals 0, 30 and 60% or 0, 40 and 80 %.

During the tests, temperature is almost constant since the concentrate recycling pipe passes through the cooling tank. The operational pressure is the one indicated by the membrane producer. Depending on the type of filtration:

- UF (2,1 bar)

- NF (6,9 bar)

- RO (13,8 bar)

Results presented effluents by effluents are:

- flow rates normalized at 25°C at increasing feed concentrations

- quality of the permeate sampled

- trend of the TOC value in the permeate compared with the TOC in the feed at the same feed concentration level

##### Second characterization –PS

At the end of the concentration effect test, a second characterization is performed as described above (§ 3.2.3.2.1).

Comparing the two characterization’s flow rate, it is possible to evaluate if permanent fouling phenomena occurred during the filtration. Comparing the second characterization flow rate with the flow rate decrease normally observed during the concentration effect test, it is possible to evaluate whether such a decrease is due to

The tables reported for each run are:

- table of flow rates determined at varying temperatures for each membrane tested, for the pressure values in the range (as for the first characterization)

- table of percentage decrease in flow rate in comparison with the first one.

##### Conclusions on the pilot scale run

At the end of the series of run described above (§3.2.3.2.) a general conclusion on the behaviour of the membrane with the specific effluent is reported and represented by:

- general comparison of flow rates registered during all the trials;

- quality of the permeate and percentage abatement of the main parameters;

- for train treatment UF+NF and UF+RO a combined overall efficiency is reported.

#### Data elaboration

In the following, elaborations to normalise the data collected during the experimental campaigns are reported, with reference to temperature and TOC.

##### Temperature -normalised flow rates

During the trials, the temperature of the feed can not be completely maintained at constant values so the permeate flow rate has to be related to different temperatures. Temperature is greatly influencing the flow rate: a normalization at a fixed reference temperature is therefore required.

The formula (Glutina et al., 2000) used to normalized at 25 °C the flow rates obtained at different temperatures is the following:

QRIFERIMENTO=QMISURATA∗e−K(TMISURATA−TRIFERIMENTO)

where the value of the parameter k has to be determined.

From the characterization data on pilot scale, a reference value of permeate flow rate is related to standard pressure and temperature conditions. Permeability obtained at different temperature, at constant pressure, have been corrected applying the formula above, in order to obtain the flow rate at the reference temperature. By applying the equivalence of the permeability values (the reference one and the corrected one) it is possible to determine the k value minimising the sum of square errors between corrected values and the reference flow rate.

So, it was possible to fix a k value for each trial at constant pressure, for each membrane used. Neglectable approximation allows for using one only average k value for each membrane.

K values obtained for some membrane and used for the data elaborations, are reported in the following:

- membrane MW :  k = 0,008;

- membrane PW  :  k = 0,011;

- membrane DK  :  k = 0,029;

- membrane DL  :  k = 0,020.

Unless differently reported in the results section (chapter 4) these are the k values used in temperature corrections.

##### TOC at growing concentration of the feed

In the concentration effect test, it has been considered that the feed concentration grows together with the discharge of the permeate (not recirculated in the feed tank as in the complete recirculation test). Sampling is made at level 0%, 20%, 40%, 60% and 80% reduction on initial volume which is supposed to be the same level of increase in concentration.

More precisely, the reduction of the feed volume can be calculated considering the initial volume Vo, the final volume remaining at the end of the trial V and calculating the volum lost (comprehending the discharge and the evaporation as well) V’

V’ = (Vo – V) / 4

So, the increasing concentration levels are:

cj = (j * V’) / Vo * 100

where j =  0;1;2;3;4.

The sampling is performed in this way: a sample of feed is taken before starting the trials; j samples of permeate are taken during the trial; at the end, a sample of feed remaining and of concentrate both at the maximum concentration are taken.

Analysing the TOC content in the samples, it is possible to extrapolate the growing of TOC concentration in the feed during the trial:

- It is considered that the volume of permeate discharged has an average TOC content:

TOC j, j+20  = (TOC j + TOC j+20) /2

Where j = 0; 20; 40; 60 and TOC j e TOC j+20 are the TOC concentration measured on the samples at j% and at j+20% respectively.

- Knowing the volume discharged and the TOC content in the samples, through mass balance evaluation it is possible to determine the theoretical TOC content in the feed during the trial, in the hypothesis that no accumulation of organic matter occurred on the membrane surface during the filtration.

- Comparing the theoretical determinated TOC with the one measured, for the feed at the maximum concentration, and considering a perfect proportional dependency between TOC accumulated on the membrane and TOC in the feed, a correlation can be found between feed volume and mass TOC accumulated.

- Furthermore, subtracting from the theoretical mass balanced TOC values the part of TOC accumulated on the membrane (expressed as concentration) it is possible to extrapolate the TOC content in the feed at different concentration levels.

In such way, it is possible to obtain a correlation between TOC in the feed and TOC in the permeate at different concentration levels and the percentage abatement at growing feed concentration, as well.

In order to verify the reliability of the method, during one of the trials samples of the feed have been collected. In the Table 13, Figure 12: Comparison between simulated and measured TOC  and Figure 13 are reported the correlation between theoretical expected values and those measured.

Table 13: TOC content in the feed

Figure 12: Comparison between simulated and measured TOC

Figure 13: Measured TOC vs. simulated TOC with calibrating line (slope =0.94, r2=0.96)

#### Technical/economical evaluation parameters

The results of various textile effluents tested on different membrane on lab and pilot scale (chapter 4) have to be elaborated to obtain operational parametres and make technical economical evaluations. Extreme variability in effluents characteristics and behaviour requires a multi parameter evaluation of the performances showed and, due to the pilot experimental equipment scale, up-scaling extrapolations are necessary.

Concerning the fluidodynamic of the system, which is basic to allow for a continual and cost-effective operation, the test carried out are described in § 3.2.3.1. and 3.2.3.2. On the flow rate measured during the tests, the following parameters have been calculated:

- I1 = Q0/Q1*100 - membrane/effluent affinity: flow rate decrease passing from pure water (Q1 during the first characterization) to real effluent filtration (Q0 initial flowrate in the concentration effect test).

Evaluation of the affinity existing between membrane and a specific effluent. It is represented by I1 (higher where I1 is closer to 100%). In fact, the maximum possible flow rate is the one obtained during the pure water filtration, any decrease registered passing to real effluents is index of compounds affecting the membrane performance (e.g. compounds increasing the polarisation of the membrane).

- I2 = (Q0 - Q80)/Q0 *100, - recovery index: percentile loss of flow rate during the concentration effect test (at increasing feed concentrations).

At increasing feed concentration, the general operating conditions of a full scale plant are simulated. Observing the decrease in flow rate with time, it is possible to determine which is the suggestible level of recovery factor (i.e. how much volume of permeate can be obtained as a percentage of the feed voume).

- I3 = (Q1 - Q2)/Q1*100 - fouling tendency: percentile loss of pure water filtration flow rate after the run in reference to the one calculated before (difference between 1st and 2nd characterization).

Performing a second characterization after the runs with real effluent it is possible to determine whether a simple rinsing with water is able to recovery the initial maximum flow rate, indicating that no permanent clogging occurred on the surface of the membrane. On the contrary, when the flow rate during the second characterization is sensibly lower than the first one, it indicates that a chemical washing is needed to recovery the maximum initial flow rate. On the base of I3 value it is possible to evaluate the number of hours that the plant can operate without the need of a chemical washing.

Based on the data on fluxes measured in each experimental run, an extrapolation on modular values (on 1 m2 of membrane surface) permitted to calculate the volume of permeate obtainable and the number of washing operations required per day.

Where I2 is inferior to 10%, it was supposed that a 90% recovery factor is reachable; when 10% < I2 < 25% the recovery factor is fixed at 80% and where I2 > 25% not more than 70% recovery was supposed.

By extrapolation of I3, in the hypothesis of a linear dependence between volume filtrated and reduction of flow rate, the hours of operation before washing was calculated (50% of flow decrease being considered as a tolerable value before washing is required).

In chapter 4, for each group of effluent treated, a final capital and operational costs evaluation is reported.

The treatment design was carried out taking into account: treatment plants complete of sand filtration membrane filtration and washing equipment, installation cost, commercial spiral wound modules 25 m2 (UF) and 32 m2 (NF), as reported in Table 14. Chemicals, consumables and energy costs. The calculation was carried out for each effluent, in four different scenarios of company size (plant treatment capacity ranging from 10000 m3/year to 250000 m3/year). In the following, an example of  costs calculation table (plant capacity: 10000: m3/year) is given. The cost trend at varying plant capacity (the same trend was evidenced for all the effluents) shows a deep decrease between 10000 m3/year and 50000 m3/year and slight further decrease at increasing plant size (100000 m3/year – 250000 m3/year).

Table 14: Example of costs’ evaluation table

|  | Items | Duration | Cost per item | Cost per year | Cost per m3 |
| --- | --- | --- | --- | --- | --- |
|  |  | years | (EURO) | (EURO/year) | (EURO/m3) |
| Sand filtration |  |  |  |  |  |
| Safety filtration |  |  |  |  |  |
| PLC |  |  |  |  |  |
| UF plant |  |  |  |  |  |
| NF plant |  |  |  |  |  |
| Washing equipment |  |  |  |  |  |
| Total Capital Cost |  |  |  |  |  |
| Installation (% TCC) |  |  |  |  |  |
| Membrane UF |  |  |  |  |  |
| Membrane NF |  |  |  |  |  |
| Filtering cartridges |  |  |  |  |  |
| Washing reactives UF |  |  |  |  |  |
| Washing reactives NF |  |  |  |  |  |
| Energy UF |  |  |  |  |  |
| Energy NF |  |  |  |  |  |
| Total |  |  |  |  |  |

In chapter 4, for each group of effluent treated, a final capital and operational costs evaluation is reported.

### Membrane cleaning and maintenance

Membranes undergo a chemical washing when the flow rates of the second characterization, performed at the end of the trials with real effluent, are at least 15% inferior to those of the preliminary characterization.

Chemical washing is operated with deionised water and detergent (0.5% in weight). The detergent, type DTM14, is a mix of alkali salts, surfactants and builders (in solution at 1%, pH=13). The action of the detergent is cleaning the membrane during a filtration step with complete recirculation of permeate and concentrate for 20 minutes. After other 20 minutes of pause, a second cycle of 10 minutes filtration takes place to complete the washing. Rinsing by deionised water is carried on till both the permeate and the concentrate have no foam traces. Normally, at least 50 l are required. During the washing operations, the temperature is free to grow while operational pressure is kept in the value suggested by the membrane producer.

After any use, it is important to keep the membranes in a 0.1% sodium bisulphide solution in order to inhibit bacterial grow.

## Reusability evaluations

The treated effluent, i.e. permeate, has been reused for different textile processes. The quality of textile materials, treated with permeate, is always compared with reference treatment for which 100% fresh process water has been used. The quality of the process water is given in Table 15.

Table 15: Process water quality

|  | unity | process water Centexbel | process water Lariana |
| --- | --- | --- | --- |
| alkalinity | mg/l |  | 79 |
| hardness | °F | <5 | 0.2 |
| chlorides | mg/l |  | 11 |
| sulphates | mg/l |  | 32 |
| sulphides | mg/l |  | 0 |
| nitrites | mg/l |  | 1.17 |
| nitrates | mg/l |  | 1.8 |
| ammonia | mg/l |  | 0 |
| TKN | mg/l |  | 2.5 |
| colour |  | absent | absent |
| Fe (tot) | mg/l |  | 0.15 |
| pH |  | 7.6 | 7.73 |
| conductivity | µS/cm | 924 | 188 |
| TSS | mg/l |  | 0 |
| COD | mg/l | 32 | 0 |

The evaluation of the reusability of permeate has been done according to the type of treatment, i.e. bleaching, scouring, degumming, polymer charge and dyeing with different types of dyestuff.

### Pretreatment

The different pretreatments performed are:

- scouring of viscose and polyester,

- bleaching of cotton,

- degumming and polymer charge of silk.

An overview of the collected waste water for the reuse tests, the treatment of the waste water, the reuse tests and the efficiency tests is given in Table 16.

Table 16: Overview of the pretreatment reuse tests

| Fibre used for tests | Process sampled | Step | Wastewater treatment | Pretreatment performed | Efficiency tests |
| --- | --- | --- | --- | --- | --- |
| PES | Scouring at 60°C | 1st rinsing | nanofiltration | scouring | scouring efficiency degree of whiteness |
| SILK YARN | HT scouring | warm rinsing | nanofiltration | degumming polymer charge | degumming efficiency charge efficiency |
| SILK FABRIC | dark acid dyeing | 1st rinsing | nanofiltration | degumming | degumming efficiency degree of whiteness |
| VISCOSE | Dark direct dyeing | 1st rinsing | nanofiltration | scouring | scouring efficiency degree of whiteness |
| COTTON | bleaching | bleaching + rinsing | ultrafiltration + nanofiltration | bleaching | degree of polymerisation degree of whiteness |

#### Degumming efficiency

Verification of the extent of de-gumming was done by means of evaluating the presence of residual sericin on the fabrics, with a qualitative proof. For the evaluation differences in dyeing results in the scourged samples were examined in comparison to an appropriate and reliable dye (Red Sirius F3B-CLARIANT;  C.I. Direct Red 80).

The amount of sericin present indicated differences in dyeing.

The test was effected according to the conduct of procedure stated in the Technical test PTP n09. from Tessile di Como’s technical manual “Procedures in Technical Tests”

#### Charge efficiency

The verification of the efficiency of the weighing can be done either by spectrophotmetry FTIR or through gravimetric analyses. The last method was used as it determines the count of the weight of the yarn silk compared to the count of the de-gummed yarn silk.

#### Scouring efficiency

The verification of the degree of scouring was checked by means of the determination of degree of whiteness.

#### Degree of whiteness

Whiteness (=the attribute by which an object colour is judged to approach a preferred white) as measured by the test method ISO-J02:1997 is an indication of how white the textile appears to an average viewer. The formulae for calculation of whiteness is recommended by the CIE.  Because reflectance is affected by the nature of the surface of the textile, comparisons can be made only between specimens of the same type of textile measured on the same apparatus and approximately at the same moment.

Principle

The CIE tristimulus values are measured using a reflectance spectrophotometer (with one of the CIE specified geometries (in preference 45/0 or 0/45) as defined in ISO 105-J01) and the whiteness calculated from formulae based on the CIE chromaticity coordinates for CIE illuminant D65 and 1964 10° observer.

The whiteness index (W10) is calculated based on the equation mentioned in ISO 105-J01:1997.  The higher the value of W10 the greater the whiteness.  Equal differences in W10 value, do not necessarily indicate equal differences in perceived whiteness. The whiteness is only applicable for specimens whose values of W10 lie withing the following units :  40< W10< 5*Y-280.

There are no tolerances mentioned in this standard, but in practice the following rule is considered :

an average experienced viewer is capable in distinguishing the difference between 5 whiteness index units.

#### Degree of polymerisation (DP)

The average degree of polymerisation of textile fibres gives an indication of the average length of a polymer. The length of a polymer is characterised by the number of monomers. Bleaching the cotton destroys partly the polymer chain which results in a decrease of the polymerisation degree.

Typical values for DP are:

| Fibre | DP |
| --- | --- |
| natural fibres:cotton, flax, ramine acceptably bleached cotton regenerated cellulose polynosic viscose | 2300-3000 1500-2000 1000-1200 250-400 |

The degree of polymerisation of a fibre is directly proportional to the viscosity of its solution. In the test a weighed sample of textile material is dissolved in cupriethylenediamine (cuen) in a standard capillary viscometer. The viscometer must be filled completely to exclude air and covered to prevent exposure to light, whilst controlled agitation is given over 16 h. The viscometer and contents are then brought to 20°C in a thermostatically controlled bath and the rate of flow through the capillary measured. The principle of the test is that during dissolution no further breakdown of the cellulose molecular chain structure will occur. Long-chain material, i.e. with low damage, will provide a highly viscous solution, hence low fluidity. The relationship between DP and fluidity (F) for cotton is given by the equation:

DP=2032log10(74.35+F)/F - 573

### Dyeing

An overview of the different dyeings is given in Table 17, as well as the source of the waste water reused after a specific treatment:

Table 17: Overview of the dyeing reuse tests

| Fibre used for tests | Process sampled | Step | Wastewater Treatment | Dyeing processes performed |
| --- | --- | --- | --- | --- |
| PES | Scouring at 60°C | 1st rinsing | nanofiltration | light disperse dyeing dark disperse dyeing |
| PES | Medium disperse dyeing | rinsing | nanofiltration | light disperse dyeing dark disperse dyeing |
| PES | disperse printing | rinsing | ultrafiltration + nanofiltration | light disperse dyeing dark disperse dyeing |
| SILK YARN | HT scouring | warm rinsing | nanofiltration | light acid dyeing dark acid dyeing |
| SILK FABRIC | dark acid dyeing | 1st rinsing | nanofiltration | light acid dyeing dark acid dyeing |
| PA | dark acid dyeing | mixed sample: dyebath + rinsing | ultrafiltration + nanofiltration | light acid dyeing dark acid dyeing |
| VISCOSE | Dark direct dyeing | 1st rinsing | nanofiltration | light direct dyeing dark direct dyeing light reactive dyeing dark reactive dyeing |
| COTTON | bleaching | mixed sample: bleaching + rinsing | ultrafiltration + nanofiltration | light direct dyeing |
| COTTON | reactive dyeing | mixed sample: dyebath + rinsing | ultrafiltration + nanofiltration | light direct dyeing dark direct dyeing light reactive dyeing dark reactive dyeing |

The tests performed on the dyed fabrics are:

- colour differences, according to ISO 105-J03

- fastness to washing, according to ISO 105-C06

- fastness to rubbing, according to ISO 105-X12

#### Calculation of colour differences

The ISO 105-J03 norm provides a method for calculating the colour difference between two pieces of the same textile material, measured under the same conditions.

The reflection of a dyed textile material is measured with a specified illuminant. The measured result is via formulas transformed into 3 colour coordinates, i.e. L, a, b.

L gives an indication of the lightness

a : green/red axis

b : blue/yellow axis

The differences in colour (E) are measured with the CMC system, taking into account the subjective sensitivity of the human eye. There are no general accepted rules concerning the maximum allowed difference in colour, but differences less than 0.8 generate normally no problem.

#### Colour fastness to washing

The ISO 105-C06 specifies methods for determining the resistance of the colour of textiles to domestic or commercial laundering procedures.

A specimen of the textile in contact with specified adjacent fabric(s) is laundered, rinsed and dried. Specimens are laundered under appropriate conditions of temperature, alkalinity, bleaching and abrasive action such that the result is obtained in a conveniently short time. The abrasive action is accomplished by the use of a low liquor ratio and an approriate number of steel balls. The change in colour of the specimen and the staining of the adjacent fabric(s) are assessed by comparison with the grey scales. Hereby is:

5 = very good – no difference in colour

4 = good –little difference in colour

3 = not sufficient – remarkable difference in colour

2 = bad – big difference in colour

1 = very bad – very big difference in colour

A difference of max. 0.5 unit is not significant.

The composition of the adjacent fabrics depends on the type of fabric to be tested and the selected test conditions. For direct dyeing of cotton and acid dyeing of polyamid A2S conditions are used. For reactive dyeing of cotton and disperse dyeing of polyester C2S conditions are used. In the following tables the test conditions are given as well as the pairs of adjacent fabrics.

| Test | temp °C | liquor volume ml | sodium perborate g/l | time min | number of steel balls | adjust pH to |
| --- | --- | --- | --- | --- | --- | --- |
| A2S C2S | 40 60 | 150 50 | 1 1 | 30 30 | 10 25 | not adjusted 10.5 |

One of the adjacent fabrics shall be made of the same kind of fibre as that of the textile to be tested, and the second piee made of the fibre as indicated in the following table.

| If first piece is: | Second piece to be: |  |
| --- | --- | --- |
|  | A2S | C2S |
| cotton polyamide polyester | wool wool or cotton wool or cotton | viscose cotton cotton |

#### Colour fastness to rubbing

The ISO 105-X12 norm specifies a method for determining the resistance of the colour of textiles of all kinds to rubbing off and staining other materials. Two tests are normally made, one with a dry rubbing cloth and one with a wet rubbing cloth.

The rubbing cloth (dry or wiet) is placed flat over the end of the finger. The specimen is rubbed at a rate of one cycle per second (10 times) with a downward force of 9 N. The staining of the cotton rubbing cloths is assesses with the grey scale for staining. Hereby is:

5 = very good – no difference in colour

4 = good –little difference in colour

3 = not sufficient – remarkable difference in colour

2 = bad – big difference in colour

1 = very bad – very big difference in colour

A difference of max. 0.5 unit is not significant.

## Reuse tests

### Polyester pretreatment (scouring, double scouring, rinsing)

#### Water source

The reference tests (scouring and disperse dyeing of polyester) are performed with 100% fresh process water (Lariana).

The reuse tests for scouring and disperse dyeing of polyester are done with 100% permeate.

#### Process description scouring

The polyester fabric was subjected to scouring using the surfactant (DS100-BOZZETTO) with a concentration of 2 ml/l and sodium carbonate to a concentration of 0.5 g/l. The treatment was done at 90°C for 30 minutes.

#### Process description disperse dyeing

The scoured polyester fabric was subjected to disperse dyeing (both light and dark colour).

Dye with disperse dyes (TERASIL – CIBA)

GREY COLOR:

0.011 % BRUNO TERASIL 2RFL

0.0054 % RED TERASIL R

0.06 % BLUE TERATOP GLF

1 g/l UNIVADINA 3FLEX (CIBA)

2 g/l (NH4)2SO4

0.5 g/l CH3COOH 80%

COLOR BLUE SEA:

0.21 % YELLOW TERASIL 4G

0.065 % RED TERASIL R

2.4 % SEA TERASIL NFA

0.7 g/l UNIVADINA 3FLEX (CIBA)

2 g/l (NH4)2SO4

0.5 g/l CH3COOH 80%

After dyeing was executed a „stripping“at 70 °C for 20 minutes, with:

1 g/l ERIOPON OS (CIBA)

for the dye in grey tone and with:

1 g/l ERIOPON OS (CIBA)

3 g/l Na2S2O4

3 ml/l NaOH 36 °Be‘

for the dye in blue sea tone.

The dyes outlined above were using the dye diagram illustrated in Figure 14:

Figure 14: Disperse dyeing diagram

### Silk pretreatment (HT scouring, rinsing)

#### Water source

The reference tests (pretreatment and acid dyeing of silk) are performed with 100% fresh process water (Lariana).

The reuse tests for pretreatment and acid dyeing of silk are done with 100% permeate.

#### Process description pretreatment: degumming, polymer charge

The silk yarn was subjected to de-gumming using an emulsifying agent with a concentration of 5 ml/l and a sequestering agent with a concentration of 1 g/l. The treatment was done at 55°C for 60 minutes.

The silk yarn was subjected to weighting using Metacrylamide (80% of silk weight), ammonium sulphate (8%) and formic acid with a concentration of 5 g/l. The treatment was done at 70°C for 120 minutes.

#### Process description acid dyeing

The samples of de-gummed yarn underwent dye tests using disperse dyes. One light tone and one dark tone were reproduced.

The following is a list of the components used to make up the dye which was used in the experiment.

BEIGE COLOR:

0.02 % ACID DYESTUFFS

0.75 % EQUALIZING AGENT

0,7 g/l ACID BUFFER

0,5 g/l ANTIFOAMING AGENT

0,8 g/l SEQUESTERING AGENT

BROWN COLOR:

2 % ACID DYESTUFFS

0.75 % EQUALIZING AGENT

1,5 g/l ACID BUFFER

0,5 g/l ANTIFOAMING AGENT

0,8 g/l SEQUESTERING AGENT

### Cotton bleaching

#### Water source

The reference tests (bleaching and direct dyeing of cotton) are performed with 100% fresh process water (Centexbel).

The reuse tests, both for bleaching and direct dyeing of cotton, are done with:

- 75% permeate/25% fresh process water

- 100% permeate

#### Process description bleaching

A non-sized cotton fabric is bleached with hydrogen peroxide (3.5 ml/l), Heptol ESW (1 ml/l), Lavotan TBU (1 ml/l), NaOH (2 ml/l) according to diagram in Figure 15:

Figure 15: Bleaching diagram

The bleaching is followed by rinsing (10 min, 60°C) and cold acidifying (10 min, 20°C).

#### Process description direct dyeing

The cotton, bleached with different water sources, is subsequently dyed with direct dyestuff in a light colour shade. The recipe is chosen because differences in the quality of the bleached cotton can be easily seen in the dyed fabric.

The dyeing and rinsing of the 3 cotton fabrics is done both with 100% fresh process water and a mixture of 75% permeate + 25% process water.

Products used for direct dyeing:

- Heptol NWS: 0.3 ml/l

- Sarabid SBF: 0.4 ml/l

- NaCl: 5 g/l

- sirius grey KCGL: 0.038%

- sirius blue KCFN: 0.038%

- sirius yellow KCF: 0.025%

Diagram followed for dyeing is reported in Figure 16:

Figure 16: Direct dyeing diagram

Rinsing:

- 10 min at 40°C

- 10 min at 40°C

- 10 min at room temperature

### Disperse dyeing and printing (dyeing, printing, washing, rinsing)

#### Reuse of disperse printing effluent

##### Water source

The reference tests (disperse dyeing of polyester) are performed with 100% fresh process water (Centexbel).

The reuse tests for disperse dyeing of polyester are done with:

- 75% permeate/25% fresh process water

- 100% permeate

##### Process description of disperse dyeing

A polyester fabric is dyed with disperse dyestuff both in a light and a dark colour shade.

Products used for disperse dyeing:

- dispergator SMS: 1 ml/l

- egasol SP: 2%

- meropan CIT: 2 ml/l

- bemacron yellow SD-RDL: 0.08% (light)

- bemacron orange SD-RDL: 0.01% (light)

- bemacron blue S-DGL: 0.015% (light)

- bemacron yellow S-6GF: 0.2% (dark)

- bemacron red SE-RDL: 0.4% (dark)

- bemacron marine SE-RLD: 0.85% (dark)

Diagram followed for dyeing light colour (Figure 17) and dark colour (Figure 18):

Figure 17: Disperse light dyeing diagram

Figure 18: Disperse dark dyeing diagram

Rinsing:

- reduction cleaning : 20 min at 80°C (only for dark shade)

- 10 min at 60°C

- cold acidifying bath at room temperature

#### Reuse of disperse dyeing effluent

##### Water source

The reference tests (scouring and disperse dyeing of polyester) are performed with 100% fresh process water (Lariana).

The reuse tests for scouring and disperse dyeing of polyester are done with 100% permeate.

##### Process description of scouring

The polyester fabric was subjected to scouring using the surfactant (DS100-BOZZETTO) with a concentration of 2 ml/l and sodium carbonate to a concentration of 0.5 g/l. The treatment was done at 90°C for 30 minutes.

##### Process description of disperse dyeing

The scoured polyester fabric was subjected to disperse dyeing (both light and dark colour).

Dye with disperse dyes (TERASIL – CIBA)

GREY COLOR:

0.011 % BRUNO TERASIL 2RFL

0.0054 % RED TERASIL R

0.06 % BLUE TERATOP GLF

1 g/l UNIVADINA 3FLEX (CIBA)

2 g/l (NH4)2SO4

0.5 g/l CH3COOH 80%

COLOR BLUE SEA:

0.21 % YELLOW TERASIL 4G

0.065 % RED TERASIL R

2.4 % SEA TERASIL NFA

0.7 g/l UNIVADINA 3FLEX (CIBA)

2 g/l (NH4)2SO4

0.5 g/l CH3COOH 80%

After dyeing was executed a „stripping“at 70 °C for 20 minutes, with:

1 g/l ERIOPON OS (CIBA)

for the dye in grey tone and with:

1 g/l ERIOPON OS (CIBA)

3 g/l Na2S2O4

3 ml/l NaOH 36 °Be‘

for the dye in blue sea tone.

The dyes outlined above were using the dye diagram in Figure 19:

Figure 19: Disperse dyeing diagram

### Acid dyeing (polyamide dyeing, silk dyed rinsing)

#### Reuse of acid dyeing effluent (polyamide dyeing)

##### Water source

The reference tests (acid dyeing of polyamide) are performed with 100% fresh process water.

The reuse tests for acid dyeing of polyamide are done with:

- 75% permeate/25% fresh process water

- 100% permeate

##### Process description of acid dyeing

A polyamide fabric is dyed with acid dyestuff both in a light and a dark colour shade.

Products used for acid dyeing:

- sarabid MKF: 2%

- sodium acetate: 3%

- albegal FFA: 0.5 g/l

- acetic acid: to reach pH 5.5 in dyebath

- tectilon yellow 3R: 0.05% (light), 1.25% (dark)

- tectilon red 2B: 0.03% (light), 0.9% (dark)

- tectilon blue 4R: 0.02% (light), 0.35% (dark)

Diagram followed for dyeing, as in Figure 20:

Figure 20: Acid dyeing diagram

Rinsing:

- 10 min at 30°C

- 10 min at 30°C

#### Reuse of acid dyeing effluent (silk dyeing)

##### Water source

The reference tests (degumming and acid dyeing of silk) are performed with 100% fresh process water.

The reuse tests for degumming and acid dyeing of silk are done with 100% permeate.

##### Process description of degumming

The silk fabric was subjected to de-gumming using a surfactant (formulated buffering). The fabric underwent a single scouring treatment using the surfactant (IDROSOLVAN S 40-BOZZETTO) with a concentration of 8 g/l and Sodium Carbonate to a concentration of 2 g/l. The treatment was done at 95° C for 90 minutes,  and followed by a final rinse.

##### Process description of acid dyeing

The samples of scoured silk underwent dye tests using acid dyes. A light shade and a dark shade were reproduced.

The following is a list of the components used to make up the dye which was used in the experiment.

BROWN:

0,28 % YELLOW TECTILON 4R

0,28 % RED TECTILON 2B

0,34 % BLUE TECTILON 4R

3 g/l (NH4)2SO4

3 g/l NaCl

0,5 % LIOGENE MS (CLARIANT)

GREEN:

1,20 % YELLOW TECTILON  2G

0,45 % BLUE TECTILON  4R

3 g/l (NH4)2SO4

3 g/l NaCl

0,5 % LIOGENE MS (CLARIANT)

The dyes outlined above were using the dye diagram in Figure 21:

Figure 21: Acid dyeing diagram

### Reactive dyeing

#### Water source

The reference tests for dyeing cotton with reactive and direct are performed with 100% fresh process water (Centexbel).

The reuse tests are done with:

- 75% permeate/25% fresh process water

- 100% permeate

#### Process description reactive dyeing

A cotton fabric is dyed with reactive dyestuff both in a light and a dark colour shade.

Products used for reactive dyeing:

- Heptol NWS: 0.3 ml/l

- NaCl: 45 g/l (light), 60 g/l (dark)

- sodium carbonate: 15 g/l

- bezaktiv yellow HE-4R: 0.05% (light), 1.6% (dark)

- bezaktiv red HE-3B: 0.07% (light), 1.6% (dark)

- bezaktiv marine HE-R: 0.03% (light), 0.8% (dark)

Diagram followed for dyeing (Figure 22):

Figure 22: Reactive dyeing diagram

Rinsing:

- 10 min at 65°C

- 10 min at 65°C

- soaping: 20 min at 95°C

- 10 min at 65°C

- 10 min at 20°C

#### Process description direct dyeing

A cotton fabric is dyed with direct dyestuff both in a medium and a dark colour shade.

Products used for direct dyeing:

- Heptol NWS: 0.3 ml/l

- Sarabid SBF: 0.4 ml/l

- NaCl: 5 g/l (medium), 10 g/l (dark)

- sirius grey KCGL: 0.15% (medium), 0.5% (dark)

- sirius blue KCFN: 0.15% (medium), 0.5% (dark)

- sirius yellow KCF: 0.1% (medium), 0.2% (dark)

Diagram followed for dyeing (Figure 23):

Figure 23: Acid dyeing diagram

Rinsing:

- 10 min at 40°C

- 10 min at 40°C

- 10 min at room temperature

### Direct dyeing (viscose)

#### Water source

The reference tests (scouring, direct and reactive dyeing of viscose) are performed with 100% fresh process water (Lariana).

The reuse tests are done with 100% permeate.

#### Process description scouring

The viscose fabric was subjected to scouring using the surfactant (DS100 -BOZZETTO) with a concentration of 2 ml/l and Sodium Carbonate to a concentration of 2 g/l. The treatment was done at 90° C for 30 minutes.

#### Process description direct dyeing

The samples of scoured viscose underwent dye tests using direct dyes. A light shade and a dark shade were reproduced.

GREY COLOR:

0.0067 % YELLOW SOLIAMINA LUCE LR

0.0055 % SCARLET SOLID DIRECT 4BS

0.037 % GREY SOLIAMINA LUCE TC-SL

4 g/l Na2SO4

1 g/l IRGASOL CO (CIBA)

BLUE SEA COLOR:

0.15 % YELLOW SOLIAMINA LUCE LR

0.05 % SCARLET SOLID DIRECT 4BS

2.75 % BLUE SOLIAMINA LUCE FFL

12 g/l Na2SO4

1 g/l IRGASOL CO (CIBA)

The dyes outlined above were using the following dye diagram:

#### Process description reactive dyeing

The samples of scoured viscose underwent dye tests using reactive dyes. A light shade and a dark shade were reproduced.

GREY COLOR:

0.0042 % YELLOW GOLD REMAZOL ES

0.02 % RED BRIGHT REMAZOL BB

0.054 % BLUE BRIGHT REMAZOL BB

30 g/l NaCl

2 g/l Na2CO3

BLUE SEA COLOR:

0.16 % YELLOW GOLD REMAZOL ES

0.35 % RED BRIGHT REMAZOL BB

1.5 % BLACK REMAZOL B

60 g/l NaCl

2 g/l Na2CO3

0.3 g/l NaOH 36 °Be‘

The dyes outlined above were using the following dye diagram:

After dyeing was performed a washing with 1 g/l of CIBAPON R to the temperature of 40°C for 20 minutes and rinse of the samples.

# Results and discussion

The effluents submitted to treatment tests are here presented, collected in eight homogeneus groups. Results of each experimental run are presented

## Polyester pretreatment (scouring, double scouring, rinsing)

In the present chapter, discussion and results of the experimental activities carried out on the three polyester pre-treatment effluents are reported. In the table below, the treatment carried out on each effluent is synthesized:

| Process Effluent | UF | NF | UF+NF | UF+RO |
| --- | --- | --- | --- | --- |
| Polyester Scouring (PS) | X |  | X | X |
| Polyester Double Scouring (PDS) | X |  | X | X |
| Polyester Scouring Rinsing (PSR) |  | X |  |  |

### Membrane treatment results

#### Direct NF results

Direct nanofiltration has been applied on PSR effluent. The results of the tests carried out according to the methods described above (par. 3.2.3), on bench scale and on pilot scale are here reported.

##### Bench scale NF on PSR effluent

###### Characterization of PSR/NF

Flow rate measurements at 6 bar pressure for three membranes at varying temperature and reported at 25 °C:

| P 6 bar | Membrane | T [°C] | QT [ l ·h-1·m-2 ] | k | Q25 [ l ·h-1·m-2 ] |
| --- | --- | --- | --- | --- | --- |
|  | DK | 30 | 62 | 0.028 | 54 |
|  | DL | 31 | 66 | 0.023 | 57 |
|  | HL | 30 | 65 | 0.027 | 57 |

###### Complete recirculation test of PSR/NF

Flow rate decrease passing to real effluent filtration:

| P 6 bar | Membrane | Q25 [ l · h-1· m-2 ] | Flow rate decrease [%] |
| --- | --- | --- | --- |
|  | DK | 39 | 13 |
|  | DL | 48 | 9 |
|  | HL | 46 | 12 |

Permeates quality:

|  | Feed | DL | HL | DK |
| --- | --- | --- | --- | --- |
| pH | 8.0 | 9.0 | 9.0 | 7.4 |
| Conductivity [S·cm-1] | 75 | 44 | 44 | 14 |
| Turbidity [NTU] | 2.1 | 0.4 | 0.8 | 0.8 |
| Abs  = 426 nm | 0.004 | 0.003 | 0.004 | 0.002 |
| Abs  = 558 nm | 0.002 | 0.002 | 0.003 | 0.001 |
| Abs  = 660 nm | 0.004 | 0.001 | 0.002 | 0.001 |
| Abs  = 436 nm | 0.004 | 0.003 | 0.004 | 0.002 |
| Abs  = 525 nm | 0.002 | 0.003 | 0.003 | 0.001 |
| Abs  = 620 nm | 0.003 | 0.002 | 0.002 | 0.001 |
| TOC [mg · l-1] | 23 | 12 | 10 | 7 |
| TC [mg · l-1] | 25 | 15 | 13 | 8 |
| IC [mg · l-1] | 2 | 3 | 3 | 1 |

###### Choice of the membrane for the pilot scale

Membrane DL seems to have the best fluid-dynamic affinity for maximum flow rate and minimum decrease passing from deionised water to real effluent filtration.

On the other hand, the best performance in terms of quality of the permeate (especially for the conductivity) is from membrane DK.

In this case, efficiency of treatment in terms of quality issues has been preferred, therefore the membrane DK is chosen for further investigation.

##### Pilot scale NF on PSR effluent

###### Pi. Sc.characterization of PSR/NF

Flow rates at different pressure values:

| p [ bar ] | Q30 [ l · h-1] | Q33 [ l · h-1] | Q35 [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- | --- |
| 6 | 14 | 15 | 15 | 12 |
| 6.9 | 16 | 18 | 18 | 14 |
| 9 | 20 | 22 | 24 | 18 |

###### Pi. Sc. complete recirculation test of PSR/NF

Flow rate and quality of the permeates:

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 31 | 13 | 11 |
| 15 | 34 | 15 | 12 |
| 30 | 36 | 16 | 12 |
| 45 | 39 | 18 | 12 |
| 60 | 40 | 18 | 12 |

|  | Feed | permeate 0' | permeate 60' |
| --- | --- | --- | --- |
| pH | 8.0 | 7.7 | 7.4 |
| Conductivity [S·cm-1] | 75 | 14 | 11 |
| Turbidity [NTU] | 2.1 | 0.2 | 0.3 |
| Abs  = 426 nm | 0.004 | 0.002 | 0.001 |
| Abs  = 558 nm | 0.002 | 0.001 | 0.003 |
| Abs  = 660 nm | 0.004 | 0.002 | 0.003 |
| Abs  = 436 nm | 0.004 | 0.002 | 0.001 |
| Abs  = 525 nm | 0.002 | 0.001 | 0.002 |
| Abs  = 620 nm | 0.003 | 0.002 | 0.004 |
| TOC [mg · l-1] | 16 | 4 | 4 |
| TC [mg · l-1] | 17 | 5 | 5 |
| IC [mg · l-1] | 1 | 1 | 1 |

###### Concentration effect test of PSR/NF

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 33 | 16 | 13 |
| 20 | 34 | 17 | 13 |
| 40 | 35 | 17 | 13 |
| 60 | 36 | 17 | 12 |
| 80 | 37 | 17 | 12 |

|  | Feed | perm. 0% | perm. 20% | perm. 40% | perm. 60% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 8.0 | 7.6 | 7.4 | 8.9 | 9.4 | 9.2 | 8.5 |
| Conductivity [S·cm-1] | 75 | 13 | 11 | 20 | 37 | 35 | 333 |
| Turbidity [NTU] | 2.1 | 0.5 | 0.3 | 0.4 | 0.6 | 0.3 | 22 |
| SST [mg · l-1] | < 5 | - | - | - | - | - | 12.5 |
| Abs  = 426 nm | 0.004 | 0.000 | 0.001 | 0.000 | 0.002 | 0.000 | 0.014 |
| Abs  = 558 nm | 0.002 | 0.000 | 0.003 | 0.002 | 0.001 | 0.000 | 0.008 |
| Abs  = 660 nm | 0.004 | 0.001 | 0.003 | 0.003 | 0.005 | 0.001 | 0.010 |
| Abs  = 436 nm | 0.004 | 0.001 | 0.001 | 0.000 | 0.002 | 0.000 | 0.013 |
| Abs  = 525 nm | 0.002 | 0.000 | 0.002 | 0.002 | 0.000 | 0.000 | 0.007 |
| Abs  = 620 nm | 0.003 | 0.001 | 0.004 | 0.003 | 0.005 | 0.001 | 0.009 |
| TOC [mg · l-1] | 16 | 8 | 8 | 5 | 6 | 8 | 58 |
| TC [mg · l-1] | 17 | 9 | 9 | 6 | 7 | 8 | 79 |
| IC [mg · l-1] | 1 | 1 | 1 | 1 | 1 | 1 | 20 |

♦ TOC in the feed

■ TOC in the permeate

###### Second characterization of PSR/NF

Flow rates in the second characterization and comparison between first and second characterization:

| p [ bar ] | Q30 [ l · h-1] | Q33 [ l · h-1] | Q35 [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- | --- |
| 6 | 13 | 14 | 15 | 11 |
| 6.9 | 15 | 17 | 18 | 13 |
| 9 | 20 | 21 | 23 | 17 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 6 | 12 | 11 | 8 |
| 6.9 | 14 | 13 | 7 |
| 9 | 18 | 17 | 6 |

###### Conclusions of PSR/NF

The pilot scale investigation showed that, passing from water to the real effluent nanofiltration, a light decrease in the permeate flow rate is observable (14 –12 l h-1).

The concentration effect test showed that the permeate flow rate stays almost constant (initial light increase and subsequent settling on the previous value) at varying feed concentration.

The second characterization shows a light loss in the flow rate, inferior to 10%, which showed a little clogging.

The quality of the permeate is very good, the percentile abatement are good especially in terms of suspended solids, turbidity and salinity (showing the presence of bi-trivalent salts). Organic content and colour are removed to lower level since the value in the feed is already low.

Comparison among flow rates measured in all the pilot scale trials.

Quality of the aver. permeate and percentage abatement

|  | Feed | Permeate | Abatement [%] |
| --- | --- | --- | --- |
| pH | 8.0 | 8.5 | - |
| Conductivity [S·cm-1] | 75 | 23 | 69 |
| Turbidity [NTU] | 2.1 | 0.4 | 80 |
| SST [mg · l-1] | < 5 | - | >99 |
| Abs  = 426 nm | 0.004 | 0.001 | 85 |
| Abs  = 558 nm | 0.002 | 0.001 | 40 |
| Abs  = 660 nm | 0.004 | 0.003 | 35 |
| Abs  = 436 nm | 0.004 | 0.001 | 80 |
| Abs  = 525 nm | 0.002 | 0.001 | 60 |
| Abs  = 620 nm | 0.003 | 0.003 | 7 |
| TOC [mg · l-1] | 16 | 7 | 57 |
| TC [mg · l-1] | 17 | 8 | 54 |
| IC [mg · l-1] | 1 | 1 | 16 |

#### UF results

UF has been tested both as single treatment and as a pre-treatment to NF and RO for the scouring and double scouring effluents reported above: PS and PDS. Separate description is reported in the following.

The membrane selection was not carried out by bench scale test. Nevertheless taking into account the effluents high clogging potential and results obtained on other pretreatment effluents, the membrane selected was the MW, having the highest permeability.

##### Pilot scale UF on PS effluent

###### Pi. Sc. characterization of PS/UF

Flow rates at different pressure and 28°C temperature values:

| p [ bar ] | Q28 [ l · h-1] |
| --- | --- |
| 1.4 | 42 |
| 1.9 | 50 |
| 2.3 | 57.5 |
| 2.8 | 65.5 |

###### Pi. Sc. complete recirculation test of PS/UF

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 28 | 53 | 52 |
| 20 | 30.5 | 55 | 52 |
| 40 | 32.5 | 56 | 53 |
| 60 | 34.5 | 58 | 54 |

|  | Feed | Permeate* |
| --- | --- | --- |
| pH | 7.3 | 7.9 |
| Conductivity [S·cm-1] | 544 | 398.5 |
| Turbidity [NTU] | 64 | 0.3 |
| Abs  = 426 nm | 0.012 | 0 |
| Abs  = 558 nm | 0.004 | 0.001 |
| Abs  = 660 nm | 0.004 | 0.002 |
| SST (mg l-1) | 15.2 | - |
| TOC [mg · l-1] | 481.1 | 119.8 |
| TC [mg · l-1] | 529.0 | 157.6 |
| IC [mg · l-1] | 47.9 | 37.8 |

*Aver. permeate during the complete recirculation test

###### Concentration effect test of PS/UF

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 25.5 | 50 | 50 |
| 20 | 27 | 51 | 51 |
| 40 | 29 | 53 | 51 |
| 60 | 31 | 54 | 52 |
| 80 | 33.5 | 56 | 52 |

|  | Feed | perm. 0% | perm. 20% | perm. 40% | perm. 60% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 7.3 | 7.9 | 8.3 | 8.3 | 8.3 | 8.5 | 8.5 |
| Conductivity [S·cm-1] | 544 | 398.5 | 425 | 460 | 510 | 586 | 750 |
| Turbidity [NTU] | 64 | 0.3 | 0.5 | 0.2 | 0.8 | 0.4 | >200 |
| SST [mg · l-1] | 15.2 | - | - | - | - | - | 63 |
| Abs  = 426 nm | 0.012 | 0 | 0.003 | 0.002 | 0.006 | 0.002 | 0.094 |
| Abs  = 558 nm | 0.004 | 0.001 | 0 | 0.002 | 0.004 | 0.004 | 0.044 |
| Abs  = 660 nm | 0.004 | 0.002 | 0.003 | 0.002 | 0.004 | 0.005 | 0.029 |
| TOC [mg · l-1] | 481.1 | 119.8 | 117.8 | 121.6 | 121 | 123.3 | 1292 |
| TC [mg · l-1] | 529.0 | 157.6 | 156.9 | 162.5 | 164.9 | 171.8 | 1346 |
| IC [mg · l-1] | 47.9 | 37.8 | 39.1 | 40.9 | 43.9 | 48.6 | 53.8 |

♦ TOC in the feed

■ TOC in the permeate

###### Second characterization of PS/UF

Flow rates in the second characterization and comparison between first and second characterization:

| p [ bar ] | Q28 [ l · h-1] |
| --- | --- |
| 1.4 | 40.5 |
| 1.9 | 49 |
| 2.3 | 55.5 |
| 2.8 | 63 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 2.1 | 53 | 51 | 4 |

###### Conclusions of PS/UF

During the ultrafiltration of real effluent with complete recirculation on pilot scale, a slight flow rate increase, compared to the value obtained with pure water filtration, occurred. The reason of such strange behaviour seems to be related to an uncomplete conditioning not enabling to reach the actual maximum flux value during the first characterization.

The concentration effect test showed that the flow rate stays almost constant. During the second characterization, a light loss of flow rate occurred.

Despite the good removals obtained for all the pollutants, the quality of the utrafiltered effluent is clearly non acceptable for reusing in textile process.

Comparison among flow rates measured in all the pilot scale trials

|  | Feed | Permeate UF | Abatement % |
| --- | --- | --- | --- |
| pH | 7.3 | 8.3 | - |
| Conductivity [S·cm-1] | 544 | 476 | 13 |
| Turbidity [NTU] | 64.0 | 0.4 | 99 |
| SST (mg l-1) | 15.2 | 0.0 | >99 |
| Abs  = 426 nm | 0.012 | 0.003 | 75 |
| Abs  = 558 nm | 0.004 | 0.002 | 50 |
| Abs  = 660 nm | 0.004 | 0.003 | 25 |
| TOC [mg · l-1] | 481 | 121 | 75 |
| TC [mg · l-1] | 529 | 163 | 69 |
| IC [mg · l-1] | 48 | 42 | 13 |

The permeate effluent from ultrafiltration is submitted to nanofiltration as described in § 4.1.1.3.1 and to RO described in § 4.1.1.4.1.

##### Pilot scale UF on PDS effluent

###### Pi. Sc. characterization of PDS/UF

Flow rates at different pressure and 27°C temperature values:

| p [ bar ] | Q27 [ l · h-1] |
| --- | --- |
| 1.4 | 39 |
| 1.9 | 47 |
| 2.3 | 52 |
| 2.8 | 60 |

###### Pi. Sc. complete recirculation test of PDS/UF

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 25 | 42 | 42 |
| 20 | 27 | 43 | 42 |
| 40 | 31 | 41 | 39 |
| 60 | 33 | 42 | 40 |

|  | Feed | Permeate* |
| --- | --- | --- |
| pH | 6.8 | 7 |
| Conductivity [S·cm-1] | 552 | 395 |
| Turbidity [NTU] | 59 | 0.8 |
| Abs  = 426 nm | 0.128 | 0.004 |
| Abs  = 558 nm | 0.068 | 0.002 |
| Abs  = 660 nm | 0.047 | 0.002 |
| SST (mg l-1) | 2 | - |
| TOC [mg · l-1] | 737 | 304 |
| TC [mg · l-1] | 756 | 316 |
| IC [mg · l-1] | 19 | 12 |

*Aver. Permeate during the complete recirculation test

###### Concentration effect test of PDS/UF

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 33 | 46 | 43 |
| 20 | 34.5 | 47 | 44 |
| 40 | 36.5 | 49 | 44 |
| 60 | 38 | 49 | 44 |
| 80 | 40 | 49 | 43 |

|  | Feed | perm. 0% | perm. 20% | perm. 40% | perm. 60% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 6.8 | 7 | 7.5 | 7.6 | 7.6 | 7.7 | 7.6 |
| Conductivity [S·cm-1] | 552 | 395 | 412 | 455 | 505 | 602 | 789 |
| Turbidity [NTU] | 59 | 0.8 | 0.7 | 0.3 | 0.6 | 0.6 | 28 |
| Abs  = 426 nm | 0.128 | 0.004 | 0.002 | 0.003 | 0.004 | 0.001 | 0.054 |
| Abs  = 558 nm | 0.068 | 0.002 | 0.000 | 0.002 | 0.003 | 0.000 | 0.025 |
| Abs  = 660 nm | 0.047 | 0.002 | 0.003 | 0.001 | 0.003 | 0.001 | 0.014 |
| SST [mg · l-1] | 2 | - | - | - | - | - | 6 |
| TOC [mg · l-1] | 737 | 304 | 306 | 316 | 330 | 356 | 1710 |
| TC [mg · l-1] | 756 | 316 | 317 | 327 | 342 | 368 | 1724 |
| IC [mg · l-1] | 19 | 12 | 11 | 11 | 12 | 13 | 14 |

♦ TOC in the feed

■ TOC in the permeate

###### Second characterization of PDS/UF

Flow rates in the second characterization and comparison between first and second characterization:

| p [ bar ] | Q27 [ l · h-1] |
| --- | --- |
| 1.4 | 30 |
| 1.9 | 38 |
| 2.3 | 40 |
| 2.8 | 47 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 2.1 | 49 | 39 | 20.4 |

###### Conclusions of PDS/UF

During the ultrafiltration of real effluent with complete recirculation on pilot scale, a significant flow rate decrease, compared to the value obtained with water filtration, occurred.

The concentration effect test showed that the flow rate stays almost constant. During the second characterization, a high loss of flow rate occurs.

The removals obtained for all the pollutants are quite good but the quality of the ultrafiltered effluent is clearly non acceptable for reusing in textile processes.

Comparison among flow rates measured in all the pilot scale trials

|  | Feed | Permeate UF | Abatement % |
| --- | --- | --- | --- |
| pH | 6.8 | 7.5 | - |
| Conductivity [S·cm-1] | 552 | 474 | 14 |
| Turbidity [NTU] | 59.0 | 0.6 | 99 |
| SST (mg l-1) | 2 | - | >99 |
| Abs  = 426 nm | 0.128 | 0.003 | 98 |
| Abs  = 558 nm | 0.068 | 0.001 | 99 |
| Abs  = 660 nm | 0.047 | 0.002 | 96 |
| TOC [mg · l-1] | 737 | 322 | 56 |
| TC [mg · l-1] | 756 | 334 | 56 |
| IC [mg · l-1] | 19 | 12 | 37 |

The permeate effluent from ultrafiltration is submitted to nanofiltration as described in § 4.1.1.3.2. and to RO described in 4.1.1.4.2.

#### UF+NF results

The choice of the membrane to be used for the treatment was not performed on bench scale; the model DK was selected for its better removal of organics and salts as evidenced on similar effluents.

##### Pilot scale NF on PS effluent after UF

###### Pi. Sc. characterization of PS/NF

Flow rates at different pressure values, measured at 29° C:

| p [ bar ] | Q29 [ l · h-1] |
| --- | --- |
| 6 | 16 |
| 6.9 | 17 |
| 9 | 23 |

###### Pi. Sc. complete recirculation test of PS/NF

Flow rate vs. time and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 31.5 | 17 | 14 |
| 20 | 34 | 19 | 14 |
| 40 | 37.5 | 20 | 14 |
| 60 | 40 | 21 | 14 |

|  | Feed | Permeate * |
| --- | --- | --- |
| pH | 8 | 6.8 |
| Conductivity [S·cm-1] | 442 | 42 |
| Turbidity [NTU] | 0.8 | 0.1 |
| SST [mg · l-1] | - | - |
| Abs  = 426 nm | 0.007 | 0.000 |
| Abs  = 558 nm | 0.003 | 0.000 |
| Abs  = 660 nm | 0.004 | 0.000 |
| TOC [mg · l-1] | 158 | 66 |
| TC [mg · l-1] | 211 | 72 |
| IC [mg · l-1] | 53 | 6 |

*Aver. Permeate during the complete recirculation test

###### Concentration effect test of PS/NF

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 21.5 | 12 | 13 |
| 20 | 28.5 | 16 | 14 |
| 40 | 35 | 18 | 14 |
| 60 | 41 | 21 | 13 |
| 80 | n. a. | n. a. | n. a. |

|  | Feed | perm. 0% | perm. 20% | perm. 40% | perm. 60% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 8 | 6.8 | 6.9 | 7.5 | 7.5 | 8 | 8.6 |
| Conductivity [S·cm-1] | 442 | 42 | 49 | 68 | 105 | 182 | 1570 |
| Turbidity [NTU] | 0.8 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 1.8 |
| SST [mg · l-1] | - | - | - | - | - | - | - |
| Abs  = 426 nm | 0.007 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.016 |
| Abs  = 558 nm | 0.003 | 0.000 | 0.000 | 0.000 | 0.002 | 0.000 | 0.009 |
| Abs  = 660 nm | 0.004 | 0.000 | 0.000 | 0.002 | 0.002 | 0.000 | 0.008 |
| TOC [mg · l-1] | 158 | 66 | 73 | 95 | 121 | 123 | 344 |
| TC [mg · l-1] | 211 | 72 | 80 | 103 | 134 | 144 | 535 |
| IC [mg · l-1] | 53 | 6 | 7 | 8 | 13 | 21 | 191 |

♦ TOC in the feed

■ TOC in the permeate

###### Second characterization of PS/NF

Flow rates in the second characterization and comparison between first and second characterization:

| p [ bar ] | Q29 [ l · h-1] |
| --- | --- |
| 6 | 16 |
| 6.9 | 18 |
| 9 | 23 |

| p [bar] | Q25 caratt. [ l · h-1] | Q25 II caratt. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 6.9 | 16 | 16 | 0 |

###### Conclusions of PS/NF

The pilot scale investigation showed, passing from water to the real effluent, a sensible decrease in the flow rate.

The value can be considered constant during the test at increasing feed concentration.

The second characterization evidences no loss in the flow rate, which shows no clogging phenomenon.

The undifferentiated reuse of the permeate seems to be difficult due to the high value of residual DOC.

SST, turbidity and colour are almost completely removed in the UF together with a good fraction of organic carbon. The overall efficiency of the treatment train is very high but the organic content in the feed is too high to match the standards for reuse.

Comparison among flow rates measured in all the pilot scale trials.

Quality of the aver. permeate and percentage abatement

|  | Feed | Permeate | Abatement % |
| --- | --- | --- | --- |
| pH | 8 | 7.34 | - |
| Conductivity [S·cm-1] | 442 | 89.2 | 80% |
| Turbidity [NTU] | 0.8 | 0.08 | 90% |
| SST [mg · l-1] | - | - | - |
| Abs  = 426 nm | 0.007 | 0 | >99% |
| Abs  = 558 nm | 0.003 | 0.0004 | 87% |
| Abs  = 660 nm | 0.004 | 0.0008 | 80% |
| TOC [mg · l-1] | 158 | 95.6 | 39% |
| TC [mg · l-1] | 211 | 106.6 | 49% |
| IC [mg · l-1] | 53 | 11 | 79% |

Overall removal efficiency of the train UF + NF, obtained combining the results of the single treatments:

|  | Abatement % UF | Abatement % NF | Overall Efficiency % |
| --- | --- | --- | --- |
| pH | - | - | - |
| Conductivity [S·cm-1] | 13 | 80 | 82 |
| Turbidity [NTU] | 99 | 90 | >99 |
| SST [mg · l-1] | >99 | - | >99 |
| Abs  = 426 nm | 75 | >99 | >99 |
| Abs  = 558 nm | 50 | 87 | 93 |
| Abs  = 660 nm | 25 | 80 | 84 |
| TOC [mg · l-1] | 75 | 39 | 85 |
| TC [mg · l-1] | 69 | 49 | 84 |
| IC [mg · l-1] | 13 | 79 | 82 |

##### Pilot scale NF on PDS effluent after UF

###### Pi. Sc. characterization of PDS/NF

Flow rates at different pressure values, measured at 29° C:

| p [ bar ] | Q26 [ l · h-1] |
| --- | --- |
| 6 | 14 |
| 6.9 | 16 |
| 9 | 21 |

###### Pi. Sc. complete recirculation test of PDS/NF

Flow rate vs. time and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 25 | 13 | 13 |
| 20 | 26.5 | 14 | 13 |
| 40 | 27.5 | 15 | 14 |
| 60 | 28.5 | 14 | 13 |

|  | Feed | Permeate* |
| --- | --- | --- |
| pH | 6.5 | 5.6 |
| Conductivity [S·cm-1] | 375 | 61 |
| Turbidity [NTU] | 19 | 0.2 |
| Abs  = 426 nm | 0.014 | 0.001 |
| Abs  = 558 nm | 0.007 | 0.000 |
| Abs  = 660 nm | 0.004 | 0.000 |
| TOC [mg · l-1] | 239 | 51 |
| TC [mg · l-1] | 260 | 56 |
| IC [mg · l-1] | 21 | 5 |

*Aver. Permeate during the complete recirculation test

###### Concentration effect test of PDS/NF

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 25.5 | 13 | 13 |
| 20 | 24.5 | 12 | 13 |
| 40 | 27.5 | 14 | 13 |
| 60 | 25 | 13 | 13 |
| 80 | 27 | 12 | 11 |

|  | Feed | perm. 0% | perm. 20% | perm. 40% | perm. 60% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 6.5 | 5.6 | 5.8 | 6 | 6.3 | 7 | 7.3 |
| Conductivity [S·cm-1] | 375 | 61 | 43 | 55 | 74 | 150 | 1358 |
| Turbidity [NTU] | 19 | 0.2 | 0.1 | 0.2 | 0 | 0.2 | 9.7 |
| Abs  = 426 nm | 0.014 | 0.001 | 0.001 | 0.000 | 0.006 | 0.004 | 0.011 |
| Abs  = 558 nm | 0.007 | 0.000 | 0.001 | 0.000 | 0.000 | 0.001 | 0.004 |
| Abs  = 660 nm | 0.004 | 0.000 | 0.000 | 0.000 | 0.005 | 0.000 | 0.002 |
| TOC [mg · l-1] | 239 | 51 | 50 | 63 | 72 | 122 | 925 |
| TC [mg · l-1] | 260 | 56 | 54 | 68 | 77 | 129 | 956 |
| IC [mg · l-1] | 21 | 5 | 4 | 5 | 5 | 7 | 31 |

♦ TOC in the feed

■ TOC in the permeate

###### Second characterization of PDS/NF

Flow rates in the second characterization and comparison between first and second characterization:

| p [ bar ] | Q26 [ l · h-1] |
| --- | --- |
| 6 | 12 |
| 6.9 | 14 |
| 9 | 18 |

| p [bar] | Q25 caratt. [ l · h-1] | Q25 II caratt. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 6.9 | 16 | 14 | 12 |

###### Conclusions of PDS/NF

The pilot scale investigation showed, passing from water to the real effluent a sensible decrease in the flow rate and a further decrease of the value was observed during the test at increasing feed concentration (over 60%).

The second characterization (permeate flow rate sensibly lower than the first) confirms that a significant part of the flux decline is due to material accumulation on the membrane surface.

SST, turbidity and colour are almost completely removed in the UF. The overall efficiency of the treatment train is very high but the high organic content in the feed makes it necessary to do further reusability evaluation.

The quality of the NF permeate seems anyway promising for reuse because most of the residual TOC is probably related to the acetic acid used in the process receipt to neutralize the alkaline scouring bath.

Comparison among flow rates measured in all the pilot scale trials:

Quality of the aver. permeate and percentage abatement:

|  | Feed | Permeate | Abatement % |
| --- | --- | --- | --- |
| pH | 6.5 | 6.14 | - |
| Conductivity [S·cm-1] | 375 | 76.6 | 80% |
| Turbidity [NTU] | 19 | 0.14 | 99% |
| Abs  = 426 nm | 0.014 | 0.002 | 83% |
| Abs  = 558 nm | 0.007 | 0.000 | 94% |
| Abs  = 660 nm | 0.004 | 0.001 | 75% |
| TOC [mg · l-1] | 239 | 71.6 | 70% |
| TC [mg · l-1] | 260 | 76.8 | 70% |
| IC [mg · l-1] | 21 | 5.2 | 75% |

Overall removal efficiency of the train UF + NF, obtained combining the results of the single treatments:

|  | Abatement % UF | Abatement % NF | Overall Efficiency % |
| --- | --- | --- | --- |
| pH | - | - | - |
| Conductivity [S·cm-1] | 14 | 80 | 82 |
| Turbidity [NTU] | 99 | 99 | >99 |
| SST [mg · l-1] | >99 | - | >99 |
| Abs  = 426 nm | 98 | 83 | >99 |
| Abs  = 558 nm | 99 | 94 | >99 |
| Abs  = 660 nm | 96 | 75 | 99 |
| TOC [mg · l-1] | 56 | 70 | 87 |
| TC [mg · l-1] | 56 | 70 | 87 |
| IC [mg · l-1] | 37 | 75 | 85 |

#### UF+RO results

The membrane used is SG by Osmonics, Inc. having the highest permeability among the RO membranes suitable for industrial effluents.

##### Pilot scale RO on PS effluent after UF

###### Pi. Sc. characterization of PS/RO

Flow rates at different pressure values, measured at 29° C:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 6 | 2.1 |
| 10 | 3.6 |
| 13.8 | 5.2 |

###### Pi. Sc. complete recirculation test of PS/ RO

Flow rate vs. time and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 23.5 | 2.3 | 2.4 |
| 30 | 25.5 | 3.4 | 3.4 |
| 60 | 33.5 | 5.2 | 4.1 |

|  | Feed | Permeate* |
| --- | --- | --- |
| pH | 7.8 | 6.2 |
| Conductivity [S·cm-1] | 410 | 15 |
| Turbidity [NTU] | 2.2 | 0.2 |
| Abs  = 426 nm | 0.010 | 0.000 |
| Abs  = 558 nm | 0.010 | 0.001 |
| Abs  = 660 nm | 0.009 | 0.001 |
| TOC [mg · l-1] | 178 | 3 |
| TC [mg · l-1] | 235 | 6 |
| IC [mg · l-1] | 57 | 3 |

*Aver. Permeate during the complete recirculation test

###### Concentration effect test of PS/ RO

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 41.5 | 5.2 | 3.2 |
| 20 | 26 | 3 | 2.9 |
| 40 | 30 | 3.7 | 3.2 |
| 60 | 34 | 3.1 | 2.4 |
| 70 | 25 | 3.3 | 3.3 |

|  | Feed | perm. 0% | perm. 20% | perm. 40% | perm. 60% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 7.8 | 6.2 | 6.2 | 6.6 | 6.1 | 6.4 | 4.4 |
| Conductivity [S·cm-1] | 410 | 15 | 10 | 12 | 13 | 18 | 1877 |
| Turbidity [NTU] | 2.2 | 0.2 | 0.1 | 0 | 0.2 | 3 | 4.5 |
| Abs  = 426 nm | 0.010 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.032 |
| Abs  = 558 nm | 0.010 | 0.001 | 0.000 | 0.000 | 0.001 | 0.000 | 0.013 |
| Abs  = 660 nm | 0.009 | 0.001 | 0.001 | 0.001 | 0.002 | 0.000 | 0.011 |
| TOC [mg · l-1] | 178 | 3 | 3 | 3 | 4 | 6 | 841 |
| TC [mg · l-1] | 235 | 6 | 6 | 6 | 7 | 10 | 845 |
| IC [mg · l-1] | 57 | 3 | 3 | 3 | 3 | 4 | 4 |

♦ TOC in the feed

■ TOC in the permeate

###### Second characterization of PS/ RO

Flow rates in the second characterization and comparison between first and second characterization:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 6 | 1.8 |
| 10 | 3 |
| 13.8 | 4.3 |

| p [bar] | Q25 caratt. [ l · h-1] | Q25 II caratt. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 13.8 | 5.2 | 4.3 | 17 |

###### Conclusions of PS/ RO

The flux decay with real effluent in reference to deionised water is sensible.

The permeate flow does not decrease at increasing in feed concentration.

The loss between first and second characterization is important.

The quality of the permeate is very good due to the high removals of all the parameters considered.

Comparison among flow rates measured in all the pilot scale trials.

Quality of the aver. permeate and percentage abatement

|  | Feed | Permeate | Abatement |
| --- | --- | --- | --- |
| pH | 7.8 | 6.3 | - |
| Conductivity [S·cm-1] | 410 | 13.6 | 97% |
| Turbidity [NTU] | 2.2 | 0.7 | 68% |
| Abs  = 426 nm | 0.010 | 0.000 | >99% |
| Abs  = 558 nm | 0.010 | 0.000 | 96% |
| Abs  = 660 nm | 0.009 | 0.001 | 90% |
| TOC [mg · l-1] | 178 | 3.8 | 98% |
| TC [mg · l-1] | 235 | 7 | 97% |
| IC [mg · l-1] | 57 | 3.2 | 94% |

Overall removal efficiency of the train UF + NF, obtained combining the results of the single treatments:

|  | Abatement % UF | Abatement % NF | Overall Efficiency % |
| --- | --- | --- | --- |
| pH | - |  |  |
| Conductivity [S·cm-1] | 13 | 97 | 97 |
| Turbidity [NTU] | 99 | 68 | >99 |
| SST [mg · l-1] | >99 | - | >99 |
| Abs  = 426 nm | 78 | >99 | >99 |
| Abs  = 558 nm | 45 | 96 | 98 |
| Abs  = 660 nm | 20 | 90 | 92 |
| TOC [mg · l-1] | 75 | 98 | 99 |
| TC [mg · l-1] | 69 | 97 | 99 |
| IC [mg · l-1] | 12 | 94 | 95 |

##### Pilot scale RO on PDS effluent after UF

###### Pi. Sc. characterization of PDS/RO

Flow rates at different pressure values, measured at 25° C:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 6 | 2.9 |
| 10 | 4.9 |
| 13.8 | 6.9 |

###### Pi. Sc. complete recirculation test of PDS/ RO

Flow rate vs. time and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 22 | 2.3 | 2.5 |
| 30 | 23.5 | 2.8 | 2.9 |
| 60 | 29.5 | 3.8 | 3.3 |

|  | Feed | Permeate* |
| --- | --- | --- |
| pH | 7.8 | 7.2 |
| Conductivity [S·cm-1] | 447 | 14 |
| Turbidity [NTU] | 7.4 | 0.2 |
| Abs  = 426 nm | 0.071 | 0.000 |
| Abs  = 558 nm | 0.044 | 0.000 |
| Abs  = 660 nm | 0.031 | 0.000 |
| TOC [mg · l-1] | 298 | 4 |
| TC [mg · l-1] | 331 | 7 |
| IC [mg · l-1] | 33 | 3 |

*Aver. Permeate during the complete recirculation test

###### Concentration effect test of PDS/ RO

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 38 | 3.8 | 2.6 |
| 20 | 28.5 | 2.4 | 2.2 |
| 40 | 26.5 | 2.4 | 2.3 |
| 60 | 29 | 3.3 | 2.9 |
| 70 | 29 | 3 | 2.7 |

|  | Feed | perm. 0% | perm. 20% | perm. 40% | perm. 60% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 7.8 | 7.2 | 7 | 8.7 | 7.7 | 8.6 | 7.3 |
| Conductivity [S·cm-1] | 447 | 14 | 15 | 26 | 24 | 30 | 1196 |
| Turbidity [NTU] | 7.4 | 0.2 | 0.1 | 0.4 | 0.2 | 0.4 | 5.4 |
| Abs  = 426 nm | 0.071 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.052 |
| Abs  = 558 nm | 0.044 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.035 |
| Abs  = 660 nm | 0.031 | 0.000 | 0.000 | 0.000 | 0.000 | 0.002 | 0.026 |
| TOC [mg · l-1] | 298 | 4 | 4 | 4 | 5 | 6 | 902 |
| TC [mg · l-1] | 331 | 7 | 7 | 8 | 9 | 11 | 947 |
| IC [mg · l-1] | 33 | 3 | 3 | 4 | 4 | 5 | 45 |

♦ TOC in the feed

■ TOC in the permeate

###### Second characterization of PDS/ RO

Flow rates in the second characterization and comparison between first and second characterization:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 6 | 1.8 |
| 10 | 2.8 |
| 13.8 | 4.1 |

| p [bar] | Q25 caratt. [ l · h-1] | Q25 II caratt. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 13.8 | 6.9 | 4.1 | 41 |

###### Conclusions of PDS/ RO

The flux decay with real effluent in reference to deionised water is sensible.

The permeate flow does not decrease at increasing in feed concentration.

The loss between first and second characterization is very important.

The quality of the permeate is very good due to the high removals of all the parameters considered.

Comparison among flow rates measured in all the pilot scale trials:

Quality of the aver. permeate and percentage abatement:

|  | Feed | Permeate | Abatement |
| --- | --- | --- | --- |
| pH | 7.8 | 7.84 | - |
| Conductivity [S·cm-1] | 447 | 21.8 | 95% |
| Turbidity [NTU] | 7.4 | 0.26 | 96% |
| Abs  = 426 nm | 0.071 | 0.000 | 100% |
| Abs  = 558 nm | 0.044 | 0.000 | 100% |
| Abs  = 660 nm | 0.031 | 0.000 | 99% |
| TOC [mg · l-1] | 298 | 4.6 | 98% |
| TC [mg · l-1] | 331 | 8.4 | 97% |
| IC [mg · l-1] | 33 | 3.8 | 88% |

Overall removal efficiency of the train UF + NF, obtained combining the results of the single treatments:

|  | Abatement % UF | Abatement % NF | Overall Efficiency % |
| --- | --- | --- | --- |
| pH | - | - | - |
| Conductivity [S·cm-1] | 99 | 95 | 96 |
| Turbidity [NTU] |  | 96 | >99 |
| SST [mg · l-1] | 98 | - | >98 |
| Abs  = 426 nm | 98 | >99 | >99 |
| Abs  = 558 nm | 96 | >99 | >99 |
| Abs  = 660 nm | 56 | 99 | >99 |
| TOC [mg · l-1] | 56 | 98 | 99 |
| TC [mg · l-1] | 38 | 97 | 99 |
| IC [mg · l-1] | 14 | 88 | 93 |

### Technical - economical feasibility

In the following paragraph the technical – economical aspects related to the treatment and reuse of the effluents are presented, independently from the considerations on permeates reusability exposed in the previous paragraphs.

In the table below, for all the treatments tested on polyester scouring effluents the values of three flow indexes are reported as resulted from the experimental runs. I1 describes the affinity membrane – effluent, I2 the reduction of permeate flow at increased feed concentration and I3 is an estimation of the hours of operation before washing is required.

Refer to § 3.2.3.4. to have a description of how the indexes are calculated and their influence on the economical evaluations.

In the following tables and graphs all the details of the economical evaluations are reported for each effluent and treatment tested, in § 3.2.3.4. the method applied is explained with the assumptions behind it.

It can be noted that:

- UF+RO for both the effluents tested resulted in high treatment costs also in the hypothesis of large volume of effluents to be treated.

- The other treatment trains tested UF, NF and UF+NF have shown a potentially high feasibility in terms of costs.

#### Cost estimation UF/PDS

#### Cost estimation UF/PS

#### Cost estimation UF+NF/PDS

#### Cost estimation UF+NF/PS

#### Cost estimation NF/PSR

#### Cost estimation UF+RO/PDS

#### Cost estimation UF+RO/PS

### Reuse tests results (rinsing)

#### Reuse of scouring permeate for scouring of polyester

##### Scouring efficiency

The verification of the degree of scouring was checked by means of the determination of the degree of whiteness.

| TREATMENT | DEGREE OF WHITE | x | y | Y |
| --- | --- | --- | --- | --- |
| REFERENCE | 77.0 | 0.3148 | 0.3323 | 79.9 |
| REUSE | 78.6 | 0.3142 | 0.3316 | 80.0 |

The higher the value, the more white is the sample. The measured degree of whiteness is acceptable and the differences are less than 5 units.

#### Reuse of scouring permeate for disperse dyeing of polyester

##### Colour differences

DYE WITH DISPERSE DYES (TERASIL - CIBA)

| Formula: CMC 2.0:1.0 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Substratum: 100% POLYESTER |  |  |  |  |  |
| Reference: COL. GREY – DYE WITH INDUSTRIAL WATER |  |  |  |  |  |
| Sample: COL. GREY – DYE WITH TREATED WATER |  |  |  |  |  |
|  | delE | delL | delC | delH | The sample is |
| D65/10 | 0.399 | -0.286 | 0.167 | 0.223 | + dark + pure + violet |
| A/10 | 0.356 | -0.279 | 0.041 | 0.217 | + dark + red |
| F11/10 | 0.370 | -0.285 | 0.105 | 0.212 | + dark + violet |

| Formula: CMC 2.0:1.0 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Substratum: 100% POLYESTER |  |  |  |  |  |
| Reference: COL. BLUE SEA – DYE WITH INDUSTRIAL WATER |  |  |  |  |  |
| Sample: COL. BLUE SEA – DYE WITH TREATED WATER |  |  |  |  |  |
|  | delE | delL | delC | delH | The sample is |
| D65/10 | 0.268 | -0.063 | -0.050 | 0.255 | + red |
| A/10 | 0.298 | -0.040 | -0.111 | 0.273 | + red |
| F11/10 | 0.278 | -0.038 | -0.118 | 0.249 | + dark + orange |

The variations of tone between the samples dyed in the two types of water are within the acceptable levels of tolerance as recommended in the quality standard norm of the 2003 edition of Italian Textile Association. ( i.e.: delE=1)

##### Colour fastness to washing

grey colour:

|  | DYEING IN NDUSTRIAL WATER | DYEING IN TREATED WATER |
| --- | --- | --- |
| Degradation colour: | 4-5 | 4-5 |
| Staining on: |  |  |
| Wool | 4-5 | 4-5 |
| Acrylic | 4-5 | 4-5 |
| Polyester | 4-5 | 4-5 |
| Polyamide | 4-5 | 4-5 |
| Cotton | 4-5 | 4-5 |
| Acetate | 4-5 | 4-5 |

blue sea colour:

|  | DYEING IN INDUSTRIAL WATER | DYEING IN TREATED WATER |
| --- | --- | --- |
| Degradation colour: | 4-5 | 4-5 |
| Staining on: |  |  |
| Wool | 4-5 | 4-5 |
| Acrylic | 4-5 | 4-5 |
| Polyester | 4-5 | 4-5 |
| Polyamide | 4-5 | 4-5 |
| Cotton | 4-5 | 4-5 |
| Acetate | 4-5 | 4-5 |

The differences in colour fastness expressed are not significant.

##### Colour fastness to rubbing

| DYEING IN INDUSTRIAL WATER |  | DYEING IN TREATED WATER |  |
| --- | --- | --- | --- |
| Colour fastness to rubbing |  | Colour fastness to rubbing |  |
| dry | wet | dry | wet |
| grey colour |  |  |  |
| 4-5 | 4-5 | 4-5 | 4-5 |
| blue sea colour |  |  |  |
| 4-5 | 4 | 4-5 | 4-5 |

As outlined there is no variation between colour fastness to rubbing in the samples dyed in using two types of water.

##### Conclusions: reuse of permeate for scouring and disperse dyeing of polyester

In general the in differences revealed at the end of each test is of little significance as they do not indicate any particular problem.

The results obtained with treated water, in reference to the materials used in the  laboratory can be considered equal to those obtained by using industrial water.

## Silk pretreatment (HT scouring, rinsing)

In the present chapter, discussion and results of the experimental activities carried out on the two silk pre-treatment effluents is reported. In the table below, the treatments carried out on each effluent is synthesized:

| Process Effluent | UF | NF | UF+NF |
| --- | --- | --- | --- |
| Silk HT Scouring (SS) | X |  | XX |
| Silk HT Scouring Rinsing (SSR) |  | X |  |

### Membrane treatment results

#### Direct NF results

Direct nanofiltration has been applied on SSR effluent. The results of the tests carried out according to the methods described above, on bench scale and on pilot scale are here reported.

##### Bench scale NF on SSR effluent

###### Characterization of SSR/NF

Flow rate measurements at 6 bar pressure for three membranes at varying temperature and reported at 25 °C:

| P 6 bar | Membrane | T [°C] | QT [ l ·h-1·m-2 ] | k | Q25 [ l ·h-1·m-2 ] |
| --- | --- | --- | --- | --- | --- |
|  | DK | 30 | 51 | 0.028 | 45 |
|  | DL | 28 | 57 | 0.023 | 53 |
|  | HL | 30 | 60 | 0.027 | 52 |

###### Complete recirculation test of SSR/NF

Flow rate decrease passing to real effluent filtration:

| P 6 bar | Membrane | Q25 [ l · h-1· m-2 ] | Diminuzione di portata [%] |
| --- | --- | --- | --- |
|  | DK | 37 | 17 |
|  | DL | 45 | 14 |
|  | HL | 38 | 27 |

Permeate quality:

|  | Alimento | DK | DL | HL |
| --- | --- | --- | --- | --- |
| pH | 7.1 | 6.8 | 9.0 | 8.5 |
| Conducibilità [S·cm-1] | 149 | 15 | 40 | 21 |
| Torbidità [NTU] | 4.7 | 0.3 | 0.5 | 1.6 |
| Abs  = 426 nm | 0.016 | 0.000 | 0.006 | 0.004 |
| Abs  = 558 nm | 0.008 | 0.000 | 0.007 | 0.001 |
| Abs  = 660 nm | 0.008 | 0.001 | 0.004 | 0.000 |
| Abs  = 436 nm | 0.016 | 0.000 | 0.005 | 0.004 |
| Abs  = 525 nm | 0.009 | 0.000 | 0.007 | 0.002 |
| Abs  = 620 nm | 0.008 | 0.000 | 0.005 | 0.000 |
| TOC [mg · l-1] | 136 | 15 | 21 | 16 |
| TC [mg · l-1] | 137 | 16 | 22 | 17 |
| IC [mg · l-1] | 1 | 1 | 1 | 1 |

###### Choice of the membrane for the pilot scale

Membrane HL has low fluid-dynamic affinity with the SSR as, passing from deionised water to real effluent filtration, almost 30% of flow rate is lost. DK and DL have similar behaviour.

Membrane DK and HL have better performances in terms of quality of the permeate (especially for the conductivity and colour). In terms turbidity, HL is less efficient. Organic content is removed almost at the same level from the three membranes.

In this case, a compromising choice for further investigation is membrane DK.

##### Pilot scale NF on SSR effluent

###### Pi. Sc. characterization of SSR/NF

Flow rates at different pressure values:

| p [ bar ] | Q30 [ l · h-1] | Q33 [ l · h-1] | Q35 [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- | --- |
| 6 | 13 | 14 | 15 | 11 |
| 6.9 | 15 | 17 | 18 | 13 |
| 9 | 20 | 21 | 23 | 17 |

###### Pi. Sc. complete recirculation test of SSR/NF

Flow rate vs. time and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 30 | 17 | 15 |
| 15 | 32 | 17 | 14 |
| 30 | 33 | 17 | 13 |
| 45 | 35 | 18 | 13 |
| 60 | 35 | 18 | 13 |

|  | Feed | permeate 0' | permeate 60' |
| --- | --- | --- | --- |
| pH | 7.1 | 7.3 | 7.8 |
| Conductivity [S·cm-1] | 149 | 46 | 23 |
| Turbidity [NTU] | 4.7 | 1.5 | 0.6 |
| SST [mg · l-1] | 7.5 | - | - |
| Abs  = 426 nm | 0.016 | 0.003 | 0.004 |
| Abs  = 558 nm | 0.008 | 0.004 | 0.000 |
| Abs  = 660 nm | 0.008 | 0.004 | 0.004 |
| Abs  = 436 nm | 0.016 | 0.003 | 0.005 |
| Abs  = 525 nm | 0.009 | 0.003 | 0.000 |
| Abs  = 620 nm | 0.008 | 0.005 | 0.004 |
| TOC [mg · l-1] | 136 | 45 | 24 |
| TC [mg · l-1] | 137 | 46 | 25 |
| IC [mg · l-1] | 1 | 1 | 1 |

###### Concentration effect test of SSR/NF

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 35 | 18 | 13 |
| 20 | 36 | 17 | 12 |
| 40 | 37 | 16 | 11 |
| 60 | 38 | 16 | 11 |
| 80 | 39 | 14 | 9 |

|  | Feed | perm. 0% | perm. 20% | perm. 40% | perm. 60% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 7.1 | 8.1 | 7.6 | 8.1 | 8.0 | 8.4 | 7.6 |
| Conductivity [S·cm-1] | 149 | 37 | 23 | 35 | 43 | 84 | 647 |
| Turbidity [NTU] | 19 | 0.8 | 0.6 | 0.3 | 0.7 | 0.4 | 66 |
| SST [mg · l-1] | 7.5 | - | - | - | - | - | 44 |
| Abs  = 426 nm | 0.016 | 0.002 | 0.003 | 0.003 | 0.002 | 0.002 | 0.058 |
| Abs  = 558 nm | 0.008 | 0.000 | 0.002 | 0.001 | 0.001 | 0.001 | 0.030 |
| Abs  = 660 nm | 0.008 | 0.004 | 0.002 | 0.003 | 0.003 | 0.001 | 0.022 |
| Abs  = 436 nm | 0.016 | 0.002 | 0.003 | 0.003 | 0.003 | 0.002 | 0.052 |
| Abs  = 525 nm | 0.009 | 0.000 | 0.002 | 0.000 | 0.002 | 0.001 | 0.033 |
| Abs  = 620 nm | 0.008 | 0.002 | 0.001 | 0.002 | 0.003 | 0.001 | 0.025 |
| TOC [mg · l-1] | 136 | 24 | 21 | 26 | 30 | 42 | 535 |
| TC [mg · l-1] | 137 | 25 | 22 | 27 | 30 | 43 | 568 |
| IC [mg · l-1] | 1 | 1 | 1 | 1 | 1 | 1 | 33 |

♦ TOC in the feed

■ TOC in the permeate

###### Second characterization of SSR/NF

Flow rates in the second characterization and comparison between first and second characterization:

| p [ bar ] | Q30 [ l · h-1] | Q33 [ l · h-1] | Q35 [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- | --- |
| 6 | 13 | 13 | 14 | 11 |
| 6.9 | 15 | 16 | 17 | 13 |
| 9 | 19 | 20 | 21 | 16 |

| p [bar] | Q25 caratt. [ l · h-1] | Q25 ricaratt. [ l · h-1] | Perdita % |
| --- | --- | --- | --- |
| 6 | 11 | 11 | 0 |
| 6.9 | 13 | 13 | 0 |
| 9 | 17 | 16 | 6 |

###### Conclusions of SSR/NF

The pilot scale investigation showed, passing from water to the real effluent nanofiltration, a light increase in the permeate flow rate probably due to an uncomplete conditioning not enabling to reach the actual maximum flux value during the first characterization.

The concentration effect test showed a light decrease in the flow rate at growing feed concentration till the level of 60%, over this value the decrease of flow rate is more relevant.

The second characterization evidences no loss in the flow rate, which shows no clogging phenomenon.

The quality of the permeate is good; the percentile abatements are good especially in terms of organic content (~ 80%), suspended solids, turbidity and salinity. Colour is removed over 80% and it is not visible in the permeate

Comparison among flow rates measured in all the pilot scale trials.

Quality of the aver. permeate and percentage abatement

|  | Feed | Permeate | Abatement |
| --- | --- | --- | --- |
| pH | 7.14 | 8.04 | - |
| Conductivity [S·cm-1] | 149 | 44 | 70% |
| Turbidity [NTU] | 19.10 | 0.55 | 97% |
| Abs  = 426 nm | 0.016 | 0.002 | 85% |
| Abs  = 558 nm | 0.008 | 0.001 | 88% |
| Abs  = 660 nm | 0.008 | 0.003 | 68% |
| Abs  = 436 nm | 0.016 | 0.003 | 84% |
| Abs  = 525 nm | 0.009 | 0.001 | 89% |
| Abs  = 620 nm | 0.008 | 0.002 | 78% |
| TOC [mg · l-1] | 136 | 29 | 79% |
| TC [mg · l-1] | 137 | 29 | 79% |
| IC [mg · l-1] | 1 | 1 | 12% |

#### UF results

##### Bench scale UF on SS effluent

###### Characterization of SS/UF

Flow rate measurements at 6 bar pressure for three membranes at constant temperature (25 °C):

| P | MW |  | PW |  | ER |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | T (°C) | Q (l h-1) | T (°C) | Q (l h-1) | T (°C) | Q (l h-1) |
| 1 | 31 | 237 | 30 | 148 |  |  |
| 1.5 | 30 | 352 | 30 | 213 |  |  |
| 2 | 30 | 474 | 30 | 283 | 26 | 138 |
| 2.5 | 30 | 628 | 29 | 357 | 26 | 172 |
| 3 |  |  |  |  | 25 | 209 |
| 3.5 |  |  |  |  | 24 | 206 |

###### Complete recirculation test of SS/UF

Flow rate decrease passing to real effluent filtration:

| Membrane | P (bar) | T (°C) | QT [ l · h-1· m-2 ] | Flow rate decrease [%] |
| --- | --- | --- | --- | --- |
| MW | 2.1 | 29 | 105 | 78 |
| PW | 2.1 | 21 | 20 | 92 |
| ER | 3.4 | 19 | 68 | 66 |

K=0.08

Permeates quality:

|  | Feed | 15' MW | 15' PW | 15' ER |
| --- | --- | --- | --- | --- |
| pH | 8.1 | 8.4 | 8.3 | 8.3 |
| Conductivity [S·cm-1] | 656/678 | 450 | 366 | 389 |
| Turbidity [NTU] | 36/43 | 1 | 1 | <1 |
| SST (mg l-1) | 20/21 | - | - | - |
| Abs  = 426 nm | 0.060/0.078 | 0.006 | 0.010 | 0.008 |
| Abs  = 558 nm | 0.021/0.035 | 0.000 | 0.003 | 0.001 |
| Abs  = 660 nm | 0.011/0.023 | 0.000 | 0.002 | 0.003 |
| TOC [mg · l-1] | 962/1020 | 348 | 212 | 228 |
| TC [mg · l-1] | 1037/1100 | 414 | 273 | 289 |
| IC [mg · l-1] | 75/81 | 66 | 61 | 61 |

###### Choice of the membrane for the pilot scale

The highest flow rate among the membrane tested was obtained by membrane MW followed by ER (even if the ER operational pressure is higher). The values obtained for PW are very low. Comparing these flows with the ones obtained during the characterization in all cases the loss is relevant (due to the unexpectedly high values measured in characterization). With reference to this parameter, ER is slightly better than MW and PW.

All the membranes have evidenced almost total removal of colour, suspended solids and turbidity. Membrane MW leaves in the permeates a residual organic content and conductivity significantly higher. All this considered, being UF mainly a pre-treatment in this case, the hydraulic parameters are evaluated as most important therefore MW is chosen for further investigation.

##### Pilot scale UF of SS effluent

###### Pi. Sc. characterization of SS/UF

Flow rates at different pressure and 30 °C temperature values:

| p [ bar ] | Q30 [ l · h-1] |
| --- | --- |
| 1.4 | 43 |
| 1.9 | 50 |
| 2.3 | 57 |
| 2.8 | 66 |

###### Pi. Sc. complete recirculation test of SS/UF

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 17 | 39 | 42 |
| 15 | 18 | 37 | 39 |
| 30 | 18 | 38 | 40 |
| 45 | 18 | 38 | 40 |
| 60 | 19 | 41 | 43 |

|  | Feed | Permeate 0’ | Permeate 60’ |
| --- | --- | --- | --- |
| pH | 8.0 | 7.7 | 7.7 |
| Conductivity [S·cm-1] | 617 | 444 | 443 |
| Turbidity [NTU] | 28.0 | 0.54 | 0.48 |
| SST (mg l-1) | 11 | 3 | 4 |
| Abs  = 426 nm | 0.056 | 0.005 | 0.004 |
| Abs  = 558 nm | 0.024 | 0.006 | 0.004 |
| Abs  = 660 nm | 0.015 | 0.006 | 0.004 |
| TOC [mg · l-1] | 840 | 199 | 184 |
| TC [mg · l-1] | 911 | 263.3 | 247.3 |
| IC [mg · l-1] | 71 | 64.3 | 63.3 |

###### Concentration effect test of SS/UF

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 19 | 41 | 43 |
| 20 | 19 | 40 | 42 |
| 40 | 19 | 40 | 42 |
| 60 | 19 | 39 | 41 |
| 80 | 19 | 38 | 40 |

|  | Feed | perm. 0% | perm. 20% | perm. 40% | perm. 60% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 8.0 | 8.4 | 8.5 | 8.2 | 7.6 | 7.9 | 8.1 |
| Conductivity [S·cm-1] | 617 | 435 | 472 | 480 | 577 | 618 | 849 |
| Turbidity [NTU] | 28.0 | 0.4 | 0.5 | 0.4 | 0.4 | 0.6 | 139.0 |
| SST (mg l-1) | 11 | - | - | - | - | - | 31 |
| Abs  = 426 nm | 0.056 | 0.002 | 0.006 | 0.006 | 0.000 | 0.003 | 0.229 |
| Abs  = 558 nm | 0.024 | 0.003 | 0.004 | 0.006 | 0.003 | 0.005 | 0.101 |
| Abs  = 660 nm | 0.015 | 0.003 | 0.003 | 0.007 | 0.004 | 0.005 | 0.062 |
| TOC [mg · l-1] | 840 | 198 | 197 | 224 | 217 | 293 | 2424 |
| TC [mg · l-1] | 911 | 259 | 263 | 286 | 287 | 365 | 2491 |
| IC [mg · l-1] | 71 | 61 | 66 | 62 | 70 | 72 | 67 |

♦ TOC in the feed

■ TOC in the permeate

###### Second characterization of SS/UF

Flow rates in the second characterization and comparison between first and second characterization:

| p [ bar ] | Q30 [ l · h-1] |
| --- | --- |
| 1.4 | 39 |
| 1.9 | 46 |
| 2.3 | 51 |
| 2.8 | 60 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 2.1 | 51 | 47 | 8 |

###### Conclusions of SS/UF

During the ultrafiltration of real effluent with complete recirculation on pilot scale, a flow rate slight increase, compared to the value obtained with water filtration, occurred. The reason of such strange behaviour seems to be related to an uncomplete conditioning not enabling to reach the actual maximum flux value during the first characterization.

The concentration effect test showed that the flow rate stays almost constant.

During the second characterization, a sensible loss of flow rate occurs.

Despite the good removals obtained for all the pollutants, the quality of the utrafiltered effluent is clearly non acceptable for reusing in textile process.

Comparison among flow rates measured in all the pilot scale trials

|  | Feed | Permeate UF | Abatement |
| --- | --- | --- | --- |
| pH | 8.0 | 8.1 |  |
| Conductivity [S·cm-1] | 617 | 516.4 | 16% |
| Turbidity [NTU] | 28.0 | 0.4 | 98% |
| SST (mg l-1) | 11 | - | >99% |
| Abs  = 426 nm | 0.056 | 0.0 | 94% |
| Abs  = 558 nm | 0.024 | 0.0 | 83% |
| Abs  = 660 nm | 0.015 | 0.0 | 71% |
| TOC [mg · l-1] | 840 | 225.6 | 73% |
| TC [mg · l-1] | 911 | 291.9 | 68% |
| IC [mg · l-1] | 71 | 66.3 | 6% |

The permeate effluent from ultrafiltration is submitted to nanofiltration as described in § 4.2.1.3.1.

#### UF+NF results

##### Bench scale NF on SS effluent after UF

###### Characterization of SS/NF

Flow rate measurements at 6 bar pressure for three membranes at constant temperature (25 °C):

| P 6 bar | Membrane | T [°C] | QT [ l ·h-1·m-2 ] |
| --- | --- | --- | --- |
|  | DK | 25 | 46 |
|  | DL | 25 | 60 |
|  | CK | 25 | 16 |

###### Complete recirculation test of SS/NF

Flow rate decrease passing to real effluent filtration at 6 bar pressure:

| Membrane | T (°C) | QT [ l · h-1· m-2 ] | Flow rate decrease [%] |
| --- | --- | --- | --- |
| DK | 35 | 36 | 28 |
| DL | 36 | 47 | 28 |
| CK | 23 | 4 | 75 |

K=0.026

Permeates quality:

|  | Feed | DK | DL |
| --- | --- | --- | --- |
| pH | 7.5/7.6 | 7.5 | 7.5 |
| Conductivity [S·cm-1] | 500/540 | 60 | 120 |
| Turbidity [NTU] | 0.3/0.6 | 0.3 | 0.4 |
| SST (mg l-1) | 21/28 | - | - |
| Abs  = 426 nm | 0.005/0.011 | 0.002 | 0.005 |
| Abs  = 558 nm | 0.002/0.007 | 0.004 | 0.005 |
| Abs  = 660 nm | 0.005/0.009 | 0.005 | 0.007 |
| TOC [mg · l-1] | 181/199 | 27 | 53 |
| TC [mg · l-1] | 247/272 | 37 | 74 |
| IC [mg · l-1] | 66/73 | 10 | 21 |

###### Choice of the membrane for the pilot scale

The best fluydodynamic performances among the membrane tested was obtained by membrane DL and also DK gave good results. On the contrary, CK has given so poor results was escluded from further investigation (permeate quality analysis).

Membrane DK leaves in the permeates a residual organic content and conductivity significantly lower than DL. All this considered, both DK and DL were submitted to further investigation.

##### Pilot scale NF (membrane DK) on SS effluent after UF

###### Pi. Sc. characterization of SS/NF (membrane DK)

Flow rates at different pressure values:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 6 | 12 |
| 6.9 | 14 |
| 9 | 17 |

###### Pi. Sc. complete recirculation test of SS/NF (membrane DK)

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 19 | 11 | 13 |
| 15 | 20 | 12 | 14 |
| 30 | 20 | 12 | 14 |
| 45 | 20 | 12 | 14 |
| 60 | 21 | 12 | 14 |

|  | Feed | permeate 0' | permeate 60' |
| --- | --- | --- | --- |
| pH | 7.6 | 6.7 | 7.3 |
| Conductivity [S·cm-1] | 542 | 31 | 39 |
| Turbidity [NTU] | 0.5 | 0.1 | 0.1 |
| SST (mg l-1) | - | - | - |
| Abs  = 436 nm | 0.003 | 0.000 | 0.003 |
| Abs  = 525 nm | 0.004 | 0.001 | 0.004 |
| Abs  = 620 nm | 0.004 | 0.000 | 0.002 |
| TOC [mg · l-1] | 174 | 16 | 24 |
| TC [mg · l-1] | 245 | 23 | 32 |
| IC [mg · l-1] | 71 | 7 | 8 |

###### Concentration effect test of SS/NF (membrane DK)

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 18 | 11 | 14 |
| 20 | 18 | 11 | 14 |
| 40 | 18 | 11 | 14 |
| 60 | 19 | 11 | 13 |
| 80 | 20 | 11 | 13 |

|  | Feed | perm. 0% | perm. 20% | perm. 40% | perm. 60% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 7.6 | 7.3 | 7.6 | 8.2 | 8.7 | 9.1 | 8.3 |
| Conductivity [S·cm-1] | 542 | 89 | 51 | 69 | 103 | 181 | 1550 |
| Turbidity [NTU] | 0.5 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 1.2 |
| SST (mg l-1) | - | - | - | - | - | - | - |
| Abs  = 436 nm | 0.003 | 0.000 | 0.003 | 0.000 | 0.000 | 0.000 | 0.022 |
| Abs  = 525 nm | 0.004 | 0.002 | 0.003 | 0.006 | 0.000 | 0.002 | 0.012 |
| Abs  = 620 nm | 0.004 | 0.000 | 0.001 | 0.003 | 0.000 | 0.000 | 0.011 |
| TOC [mg · l-1] | 174 | 35 | 26 | 30 | 40 | 54 | 523 |
| TC [mg · l-1] | 245 | 49 | 35 | 42 | 58 | 82 | 594 |
| IC [mg · l-1] | 71 | 14 | 9 | 12 | 18 | 28 | 71 |

♦ TOC in the feed

■ TOC in the permeate

###### Second characterization of SS/NF (membrane DK)

Flow rates in the second characterization and comparison among first, second and after washing characterization:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 6 | 12 |
| 6.9 | 14 |
| 9 | 19 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 6.9 | 14 | 14 | - |

###### Conclusions of SS/NF (membrane DK)

Flows obtained with the real effluent are similar to the maximum reference value with deionised water.

The concentration effect test showed that the flow rate stays constant at varying feed concentration till the level of increased concentration of 40%. A certain decrease in permeate flow rate is observable at higher concentrations.

During the second characterization the flow rate is as in the first one.

The quality of the permeate is good due to the very good removals of all parameters considered.

Comparison among flow rates measured in all the pilot scale trials:

Quality of the aver. permeate and percentage abatement:

|  | Feed | Permeate | Abatement |
| --- | --- | --- | --- |
| pH | 7.6 | 8.2 |  |
| Conductivity [S·cm-1] | 542 | 98.6 | 82% |
| Turbidity [NTU] | 0.5 | 0.1 | 74% |
| SST (mg l-1) | 23 | 0.1 | 99% |
| Abs  = 436 nm | 0.003 | 0.001 | 80% |
| Abs  = 525 nm | 0.004 | 0.003 | 35% |
| Abs  = 620 nm | 0.004 | 0.001 | 80% |
| TOC [mg · l-1] | 174 | 37.0 | 79% |
| TC [mg · l-1] | 245 | 53.4 | 78% |
| IC [mg · l-1] | 71 | 16.3 | 77% |

Overall removal efficiency of the train UF + NF, obtained combining the results of the single treatments:

|  | Abatement % UF | Abatement % NF | Overall Efficiency % |
| --- | --- | --- | --- |
| pH | - | - | - |
| Conductivity [S·cm-1] | 16 | 82 | 85 |
| Turbidity [NTU] | 98 | 74 | >99 |
| SST [mg · l-1] | >99 | - | >99 |
| Abs  = 426 nm | 94 | 80 | 98.8 |
| Abs  = 558 nm | 83 | 35 | 89 |
| Abs  = 660 nm | 71 | 80 | 94 |
| TOC [mg · l-1] | 73 | 79 | 94 |
| TC [mg · l-1] | 68 | 78 | 93 |
| IC [mg · l-1] | 6 | 77 | 78 |

##### Pilot scale NF (membrane DL) on SS effluent after UF

###### Pi. Sc. characterization of SS/NF (membrane DL)

Flow rates at different pressure values:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 6 | 19 |
| 6.9 | 21 |
| 9 | 28 |

###### Pi. Sc. complete recirculation test of SS/NF (membrane DL)

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 18 | 18 | 21 |
| 15 | 19 | 19 | 21 |
| 30 | 20 | 20 | 22 |
| 45 | 21 | 20 | 22 |
| 60 | 22 | 21 | 22 |

|  | Feed | permeate 0' | permeate 60' |
| --- | --- | --- | --- |
| pH | 7.6 | 7.3 | 7.8 |
| Conductivity [S·cm-1] | 554 | 44 | 62 |
| Turbidity [NTU] | 0.3 | 0.3 | 0.1 |
| Abs  = 436 nm | 0.006 | 0.001 | 0.003 |
| Abs  = 525 nm | 0.001 | 0.001 | 0.002 |
| Abs  = 620 nm | 0.001 | 0.000 | 0.002 |
| TOC [mg · l-1] | 209 | 41 | 55 |
| TC [mg · l-1] | 288 | 53 | 70 |
| IC [mg · l-1] | 79 | 12 | 15 |

###### Concentration effect test of SS/NF (membrane DL)

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 20 | 21 | 23 |
| 20 | 19 | 19 | 21 |
| 40 | 18 | 18 | 21 |
| 60 | 18 | 18 | 21 |
| 80 | 17 | 17 | 20 |

|  | Feed | perm. 0% | perm. 20% | perm. 40% | perm. 60% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 7.6 | 7.9 | 8.1 | 8.2 | 8.5 | 8.8 | 8.3 |
| Conductivity [S·cm-1] | 554 | 95 | 74 | 97 | 143 | 229 | 1518 |
| Turbidity [NTU] | 0.3 | 0.2 | 0.1 | 0.3 | 0.2 | 0.2 | 1.1 |
| Abs  = 436 nm | 0.006 | 0.002 | 0.004 | 0.004 | 0.001 | 0.002 | 0.010 |
| Abs  = 525 nm | 0.001 | 0.001 | 0.004 | 0.004 | 0.001 | 0.001 | 0.005 |
| Abs  = 620 nm | 0.001 | 0.003 | 0.001 | 0.003 | 0.000 | 0.000 | 0.002 |
| TOC [mg · l-1] | 209 | 59 | 57 | 62 | 74 | 91 | 553 |
| TC [mg · l-1] | 288 | 80 | 74 | 82 | 100 | 130 | 766 |
| IC [mg · l-1] | 79 | 21 | 17 | 21 | 26 | 40 | 214 |

♦ TOC in the feed

■ TOC in the permeate

###### Second characterization of SS/NF (membrane DL)

Flow rates in the second characterization and comparison among first, second and after washing characterization:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 6 | 18 |
| 6.9 | 21 |
| 9 | 28 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 6.9 | 21 | 21 | - |

###### Conclusions of SS/NF (membrane DL)

Flows obtained with the real effluent are similar to the maximum reference value with deionised water.

Apart from the first value measured during the concentration effect test (probably due to an overestimetion error) the permeate flux is constant during the test.

During the second characterization the flow rate is as in the first one.

All permeate flows measured with DL are sensibly higher than those with DK.

The permeate quality is quite good but lower than the one obtained with DK.

Comparison among flow rates measured in all the pilot scale trials:

Quality of the aver. permeate and percentage abatement

|  | Feed | Permeate | Abatement |
| --- | --- | --- | --- |
| pH | 7.6 | 8.3 |  |
| Conductivity [S·cm-1] | 554 | 128 | 77% |
| Turbidity [NTU] | 0.3 | 0.2 | 42% |
| SST (mg l-1) | 21 | - | >99% |
| Abs  = 436 nm | 0.006 | 0.003 | n.a. |
| Abs  = 525 nm | 0.001 | 0.002 | n.a. |
| Abs  = 620 nm | 0.001 | 0.001 | n.a. |
| TOC [mg · l-1] | 209 | 69 | 67% |
| TC [mg · l-1] | 288 | 93 | 68% |
| IC [mg · l-1] | 79 | 25 | 69% |

n.a. = not applicable due to the very low value in the feed

The overall removal efficiency of the train UF + NF, obtained combining the results of the single treatments, is reported in tab. below:

|  | Abatement % UF | Abatement % NF | Overall Efficiency % |
| --- | --- | --- | --- |
| pH | - | - | - |
| Conductivity [S·cm-1] | 16 | 77 | 81 |
| Turbidity [NTU] | 98 | 42 | 99 |
| SST [mg · l-1] | >99 | 99 | 99 |
| Abs  = 426 nm | 94 | n.a. | >94 |
| Abs  = 558 nm | 83 | n.a. | >83 |
| Abs  = 660 nm | 71 | n.a. | >71 |
| TOC [mg · l-1] | 73 | 67 | 91 |
| TC [mg · l-1] | 68 | 68 | 90 |
| IC [mg · l-1] | 6 | 69 | 70 |

### Technical - economical feasibility

In the following paragraph the technical – economical aspects related to the treatment and reuse of the effluents are presented, independently from the considerations on permeates reusability exposed in the previous paragraphs.

In the table below, for all the treatments tested on silk scouring effluents the values of three flow indexes are reported as resulted from the experimental runs. I1 describes the affinity membrane – effluent, I2 the reduction of permeate flow at increased feed concentration and I3 is an estimation of the hours of operation before washing is required.

Refer to § 3.2.3.4. to have a description of how the indexes are calculated and their influence on the economical evaluations.

In the following tables and graphs all the details of the economical evaluations are reported for each effluent and treatment tested, in § 3.2.3.4. the method applied is explained with the assumptions behind it.

It can be noted that the treatment trains tested UF, NF and UF+NF have shown a potentially high feasibility in terms of costs for both the silk scouring and the rinsing phases only.

#### Cost estimation UF/SS

#### Cost estimation UF+NF/SS

#### Cost estimation NF/SSR

### Reuse tests results (rinsing)

#### Reuse of scouring permeate for degumming of silk

##### Degumming efficiency

The verification of the degumming efficiency was checked by means of the determination of the degree of whiteness.

| TREATMENT | DEGREE OF WHITE | x | y | Y |
| --- | --- | --- | --- | --- |
| REFERENCE | 50.1 | 0.3211 | 0.448 | 79.5 |
| REUSE | 46.4 | 0.3239 | 0.3464 | 80.6 |

The higher the value, the more white is the sample. The measured degree of whiteness is acceptable and the differences are less than 5 units.

#### Reuse of scouring permeate for acid dyeing of silk

##### Colour differences

| Formula: CMC 2.0:1.0 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Substratum: yarn 100% silk |  |  |  |  |  |
| Reference: COL. BEIGE – DYE WITH INDUSTRIAL WATER |  |  |  |  |  |
| Sample: COL. BEIGE – DYE WITH TREATED WATER |  |  |  |  |  |
|  | delE | delL | delC | delH | The sample is |
| D65/10 | 0734 | -0.139 | -0.481 | -0.537 | + dark + dirty + blue |
| A/10 | 0.663 | -0.148 | -0.444 | -0.469 | + dark + dirty + blue |
| F11/10 | 0.716 | -0.154 | -0.517 | -0.472 | + dark + dirty + blue |

| Formula: CMC 2.0:1.0 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Substratum: spun 100% silk |  |  |  |  |  |
| Reference: COL. BROWN – DYE WITH INDUSTRIAL WATER |  |  |  |  |  |
| Sample: COL. BROWN – DYE WITH TREATED WATER |  |  |  |  |  |
|  | delE | delL | delC | delH | The sample is |
| D65/10 | 0.954 | 0.929 | 0.167 | 0.140 | + clear+ pure + yellow |
| A/10 | 0.933 | 0.910 | 0.186 | 0.086 | + clear+ pure + yellow |
| F11/10 | 0.952 | 0.925 | 0.188 | 0.122 | + clear+ pure + yellow |

The variations of tone between the samples dyed in the two types of water are within the acceptable levels of tolerance as recommended in the quality standard norm of the 2003 edition of Italian Textile Association. ( i.e.: delE=1)

##### Colour fastness to washing

Beige colour

|  | DYEing in INDUSTRIAL WATER | DYEing in TREATED WATER |
| --- | --- | --- |
| Degradation colour: | 4-5 | 4-5 |
| Staining on: |  |  |
| Wool | 4-5 | 4-5 |
| Acrylic | 4-5 | 4-5 |
| Polyester | 4-5 | 4-5 |
| Polyamide | 3-4 | 3-4 |
| Cotton | 4 | 4 |
| Acetate | 4-5 | 4-5 |

Brown colour:

|  | DYEing in INDUSTRIAL WATER | DYEing in TREATED WATER |
| --- | --- | --- |
| Degradation colour: | 4-5 | 4-5 |
| Staining on: |  |  |
| Wool | 4 | 4 |
| Acrylic | 4-5 | 4-5 |
| Polyester | 4 | 4 |
| Polyamide | 2 | 2 |
| Cotton | 3-4 | 3-4 |
| Acetate | 3-4 | 3-4 |

The differences in colour fastness expressed are not significant.

##### Colour fastness to rubbing

| Dyeing in INDUSTRIAL WATER |  | DYEing in TREATED WATER |  |
| --- | --- | --- | --- |
| colour fastness to rubbing |  | colour fastness to rubbing |  |
| dry | wet | dry | wet |
| beige colour |  |  |  |
| 4-5 | 4-5 | 4-5 | 4-5 |
| brown colour |  |  |  |
| 4-5 | 4-5 | 4-5 | 4-5 |

As outlined there is no variation between colour fastness to rubbing  in the samples dyed in using two types of water.

##### Conclusions: reuse of permeate for degumming and acid dyeing of silk

In general the differences revealed at the end of each test is of little significance as they do not indicate any particular problem.

The results obtained with treated water, in reference to the materials used in the  laboratory can be considered equal to those obtained by using industrial water.

## Cotton pretreatment (Bleaching, scouring, sizing)

The experimental here reported concerns: anaerobic biodegradability tests on cotton bleaching and scouring effluents, anaerobic treatment of size liquid in UASB reactor and membrane treatment of cotton bleaching line effluent

### Anaerobic treatment

#### Anaerobic biodegradability batch tests

##### Sizing liquid

According to the experimental data (see Figure 24) the organic matter present in the diluted sizing wastewater converted via VFA into methane. CODd concentration dropped from 4561 mg/l to 150-257 mg/l in a time period of 16-18 days and achieved a minimum of 60 mg/l on day 31. No VFA was present in the medium after 31 days (36 mg/l). During this period COD-CH4 raised from 0 to the maximum concentration of 4277 mg/l. The results shown in Figure 24 allow a good comparison between COD-VFA and CODd concentration. It is obvious that more than 80% organic matter in wastewater was converted into VFA. The efficiency of the treatment reached 97-98%, the anaerobic biodegradability of sizing liquid was high at the concentration applied, as the achieved removal efficiency on day 18 was 97%.

Figure 24 - Anaerobic biodegradability of sizing wastewater. Filtered COD (x), COD-VFA (∆) and COD-CH4 (○).

##### Indigo dyed cotton scouring wastewater

Anaerobic degradability test

Concentration of CODt was reduced from 5787 to 2846 mg/l at day 0, to 3787 mg/L at day 32 corresponding to a COD removal efficiency of 33.8% to 52.2%. COD was reduced around 50% at day 0. This is also explained by the fact that precipitation immediately happened after adding sodium carbonate. In the following days COD increased from 2846 to 3787 mg/L. The amount of VFA-COD increased significantly from 215 mg/l at the beginning up to a maximum concentration of 3634 mg/l at day 32, but no conversion into methane was observed. The VFA consisted of acetate, propionate, and a very small amount of butyrate (results not shown). With a pH of the solution similar to the dyeing wastewater, VFA could not convert into methane. However, the pH can not be an explanation for the low methane production. Methanogenic bacteria are inhibited at a pH below 5.5, whereas the pH of the experiment was 6.6. Colour decreased from 0.5 to 0.071A in 32 days. The results are presented in Figure 25 and Figure 26. It is shown that only a small amount of organic matter was converted to methane.

Figure 25 - Anaerobic biodegradability of scouring wastewater. Filtered COD (x), COD-VFA (∆) and COD-CH4 (○).

Figure 26 - Reduction of colour at A= 674 nm for scouring wastewater.

Effect of initial wastewater concentration on the anaerobic degradability

In the first feed, the CODd was reduced from 1212-6250 mg/l to 869-6166 mg/l corresponding to a COD removal efficiency of 26.3-85.3% for a period time of one week. Organic matter present in wastewater is converted very fast via acetate, propionate and butyrate into methane at the first day, corresponding to COD-CH4 increased from 0-1326 mg/l for R1, 0-2011 mg/l for R2, 0-2049 mg/l for R3, 0-2340 mg/l for R4, 0-2574 mg/l for R5, and 0-2789 mg/l for R6. It achieved a maximum value after 7 days in the range of 2346 mg/l for R1, 3318 mg/l for R2, 2913 mg/l for R3, 3808 mg/l for R4, 3718 mg/l for R5, and 3915 mg/l for R6. The VFA was raised up from 76-197 to 869-6113 mg/l during a period of 7 days. At the end of the experiment a significant amount of VFA remained.

Granular sludge adsorbed colour very well, which had an effect on the colour measurement. The process occurred immediately after addition of wastewater to the sludge and achieved maximum value at the first day, for instance, colour changed from 3.050-11.915A to 1.045-4865 A, except the R6 experiment, and then it was increased gradually to 2.025-5.785A at day 7. With R6, colour was increased slightly from 1.550 to 2.550 during the experimental period of 7 days. This can be explained by the presence of colloidal particles in the wastewater, causing turbidity that can affect the colour measurement.

After setting up, the pH of all bottles was in the range of 6.8-7.1. At the last day pH decreased to 6.7 for R1, 6.7 for R2, 6.6 for R3, 6.8 for R4, 6.2 for R5, and 6.3 for R6. The pH value dropped due to higher conversion rate of acidogenic bacteria compared to methanogenic bacteria and the higher the wastewater concentration the lower the pH.

In the second feed, anaerobic bacteria were already inhibited by toxicity of wastewater substrate or maybe affected by the concentration of Na2S that was added to ensure completely anaerobic conditions. Another possibility is inhibition due to precipitation of particles on sludge. Although the experimental time was expanded to 24 days all analysed parameters remained unchanged.

The CODt removal efficiency was lower at the higher COD concentration. VFA concentration still remained significant amount in medium. The results are presented in Figure 27.

Figure 27 - Biodegradability assay results for scouring wastewater, for various initial concentrations of COD (mg/l): 3010 (R1 - x), 6019 (R2 - ○), 6007filter COD (R3 - ∆), 9029 (R4 - ◊), 11575 (R5 - □), 8437filter COD (R6 - +). Top: Changes in the total COD concentration, Second: Changes in the COD-VFA concentration, Third: Methane production, Bottom: Colour removal. Bottles received a new feed on day 7.

##### Bleaching wastewater

Anaerobic degradability test

With bleaching wastewater, organic matter present in the wastewater was converted very fast via acetate, propionate butyrate. The COD-VFA concentration in the medium was high (2720 mg/l) at the end of the experiment in which acetate was the main component (about 1600 mg/l). Similar to the experiments with scouring wastewater, the conversion of VFA to methane may have been inhibited by a low pH in the medium. Although the pH was round 6.8. During the period of 32 days, the CODt was reduced from 5027 mgCODt/l to 2774 mgCODd/l corresponding to a COD removal efficiency of 52.2-58.0%. Because there was so much precipitate present in the medium, the COD reduction rate was bout 45 % in the first day, but it remained almost unchanged until day 24-32 day. Produced methane during the experimental period time was insignificant, it only achieved a maximum of 626 mg COD-CH4/l. The results are presented in Figure 28.

Figure 28 - Anaerobic biodegradability of bleaching wastewater. Filtered COD (x), COD-VFA (∆) and COD-CH4 (○).

Effect of initial wastewater concentration on the anaerobic degradability

In the first feed, the CODd was reduced from 967 to 15 mg/l, corresponding to the highest COD removal efficiency of 99.5% for R1. Next, CODd decreased in the ranges of 2797 to 689 mg/l with a removal efficiency 88.5% for R2, 4627 to 1424 mg/l corresponding to a removal efficiency 76% for R3, 7194 to 5860 mg/l corresponding to a removal efficiency removal efficiency 56% for R4, and 6704 to 6323 mg/l corresponding to a COD removal efficiency of 47% for R6 at the end of the experiment.

After adding sodium bicarbonate, immediately precipitation occurred in the medium. This explains the fact that COD decreased at day 0. Organic matter present in the wastewater was converted very fast to acetate, propionate and butyrate, but not into methane for R4 and R5. COD-VFA still remained in a significant amount in the medium, 4659 mg/l for R4 and 4489 mg/l for R5 at day 7. VFA of R1 was not present any more in medium, it was around 31 at day 0 and 7 at the end 7-247. For R2 and R3, VFA concentration increased from 101-132 to 417-856 mg/l at day 2 and the following days it decreased to 247-721 mg/l. The COD-CH4 concentration increased from 0 to 2346-3915 mg/l in 7 days.

At day 0, after setting up, the pH dropped in all cases to 6.2, 6.3, 6.6, 6.6 and 6.5 for R1, R2, R3, R4, and R5. After the first day, pH decreased in the range of 6.7-6.8 for R1, R2, and R3 and changed to 6.7 for R1, 6.8 for R2 and 7.0 for R3 at the end. With R1 and R2, pH at day 0 was 6.6 and 6.5 and decreased slightly to pH 6.3 at day 7. The pH value dropped due to the higher conversion rate of acidogenic bacteria compared to the methanogenic bacteria. A pH increase corresponds with the conversion of acetate into methane and the consequent release of HCO3-.

In the second feed, COD removal efficiency was decreased compared to the first feed. The reason was that anaerobic bacteria were already inhibited by toxicity of the wastewater or maybe affected by accumulation of the Na2S that had been added to ensure completely anaerobic conditions.

The CODt removal efficiency was lower at higher COD concentrations. Significant amounts of VFA still remained in the medium at the end of the experiment. The results are presented in Figure 29.

Figure 29 - Biodegradability assay results for bleaching wastewater, for various initial concentrations of COD (mg/l): 3004 (R1 - x), 6007 (R2 - ○), 8769 (R3 - ∆), 13409 (R4 - ◊), 11960 filter COD (R5 - □). Top: Changes in the total COD concentration, Middle: Changes in the COD-VFA concentration, Bottom: Methane production. Bottles received a new feed on day 8.

#### Anaerobic treatment of size liquid in UASB reactor

Granular Sludge was adapted after 7 days starting up with VFA mixture.  When a removal efficiency of  88-99% was achieved, operation of the reactor was continued with real wastewater.

The initial experiment with sizing wastewater was started up at HRT 15 hour and OLR of 3.2 kgCOD/m3.day. A recirculation with a recycle factor of 5 was also applied to increase contact between sludge and substrate. The initial upflow velocity was 0.5 m/h. After 5 days operation of the reactor a floating sludge and foaming phenomenon occurred which caused very low efficiency and clogging of the gas line, but did not lead to washout of sludge. It was observed that precipitates of lipid and hydrolysis products of starch were accumulated in significant amounts in the reactor during the operation time. When applying recirculation, lipid can be converted into long chain fatty acids or fat matter. In time these created a film layer that covered the sludge. The film caused granules to stick together resulting in large particles with a film layer on the outside. This sludge prevented the release of gas from the sludge bed. As a consequence, sludge was pushed out of the top of reactor. In the following seven days, the complete sludge bed floated. In order to overcome this phenomenon, recirculation was stopped, and then reactor operation was continued running with HRT 15 hour and OLR of 3.2 kg COD/m3.day, while the upflow velocity was reduced to 0.084 m/h.

##### HRT 15 hours

During the first 19 days of operation, the total concentration of influent COD ranged from 1865 mg/l to 2036 mg/l and the concentration of effluent COD decreased from 402 to 246 mg/l, corresponding to a COD removal efficiency of 78 to 88%.  Following 13 days, the treatment efficiency exceeded 80% and remained stable. Comparison of removal efficiency among CODt, CODp, and CODd, the efficiency of removal of CODd was usually higher than CODt and CODp. The data show that soluble COD was about 80% of CODt and the concentration of COD suspended solids was not significant. This indicated that anaerobic biodegradation of soluble starch was complete but the maximum treatment efficiency only reached 88%. The reason can be that the concentration of effluent COD can relate to the concentration of lipids, because biodegradation of lipids to methane was very poor and conversion of lipid into methane normally proceeds only partially (Petruy & Lettinga, 1997; Rinzema, 1988).

At the velocity 0.084 m/h almost no sludge was washed out, and therefore the concentration of SS in the effluent was low with a maximum concentration of 33 mg/l. Influent SS ranged from 29-31 mg/l. The pH of the effluent ranged from 7.10-8.15 whereas the pH of the influent was constant at a value of 8.4. Figure 30, Figure 31, and Figure 32 show values of COD, SS, VFA influent and effluent, and treatment efficiency (E%=(CODi,sol-CODe,sol)/CODi,sol) at the HRT of 15 hour.

Figure 30 - Influent and effluent COD with HRT 15 hour

Figure 31 - Influent and effluent SS, VFA with HRT 15hour

Figure 32 - COD removal efficiency with HRT 15 hour

##### HRT 12 hours

The experiment was continued with an HRT of 12 hours. Experimental conditions were the same as for the HRT of 15 hours. The total concentration of the influent COD ranged from 1742 mg/l to 2330 mg/l and the effluent COD concentration decreased from 307 to 83 mg/l, corresponding to a COD removal efficiency of 80 to 96%. The treatment efficiency was slightly increased compared to the HRT of 15 hours. When removal efficiency was gradually increased with time, suddenly, treatment efficiency dropped to 80 % at 12 days of operation and increased again the following 2 days. Concentration of effluent SS increased from 35-88 mg/l, because there was some floating sludge and precipitates present in the effluent. Concentration of influent VFA was almost unchanged during that time operation, it was about 43-49 mg/l, but effluent VFA was increased from 60-65 mg/l following 18 days of operation. Effluent pH ranged from 6.9 to 8.0 and influent pH was about 8.2-8.4. The results of the experiment are presented in Figure 33, Figure 34, and Figure 35.

Figure 33 - Influent and effluent COD with HRT 12 hour

Figure 34 - Influent and effluent SS, VFA with HRT 12hour

Figure 35 - Removal efficiency COD with HRT 12 hour

##### HRT 10 hours

At the operation regime, flow was increased to 4.8 l/day corresponding with an upflow velocity of 0.2 m/h. Treatment efficiency decreased below 70% after the first 6 days of operation with an HRT of 10 hour, but then a value of 89% was achieved which remained stable until day 21. Influent COD was less than 2000 mg/l and the effluent COD ranged from 523-240 mg/l. The effluent COD did not decrease below 200 mg/l. Concentration of SS in the effluent was higher than in the first 6 days, because of washing out of floating sludge. However, following these days the SS in the effluent decreased to around 23-33 mg/l. Concentration of influent VFA at HRT 10 hour was higher than HRT 12, and 15 hour. A possible explanation is that starch was digested partly in the stored raw wastewater at 10C. This hypothesis was supported by the observed drop of the pH of the raw wastewater from 7.5 to 6.5, and the slight increase in influent VFA. Values of effluent VFA ranged from 45-84 mg/l. Removal efficiency of lipid was increased from 31-50% in the time interval of 26 days.

The gas outlet was frequently clogged by floating granular sludge. After 38 days of operation of the reactor, the height of the sludge bed had grown to 225 mm, so half of the sludge bed was taken out keep the height at a level of 125 mm. At that time, the size of granular sludge was become larger than initial sludge (Figure 40). The reason was that some small sludge granules were aggregated to create larger sludge granules.  This adhesion was caused by the film layer. Almost all of the sludge in the reactor was covered by a film. The results are presented in Figure 36 - Figure 39.

Figure 36 - Influent and effluent COD with HRT 10 hour

Figure 37 - Influent and effluent SS, VFA with HRT 10hour

Figure 38 - Removal efficiency COD with HRT 10 hour

Figure 39 - Removal efficiency lipid with HRT 10 hour

Figure 40 - Size of sludge after 66 days of operation (HRT10h)

##### HRT 8 hours

Floating sludge was observed after 16 days of operation. Treatment efficiency dropped from 85% to 64%, the concentration of VFA in the effluent increased from 131 to 250 mg/l. Concentration of lipid in the effluent (69.7 mg/l) was higher than in the influent (89.7 mg/l), because of severe washout of sludge and precipitates in effluent. To overcome the problem, anti foaming chemical (anti foam silicon) was added to the reactor, but with no success. Then the operation regime was reset to HRT 10 hour. The results are depicted in Figure 41 - Figure 44.

Figure 41 - Influent and effluent COD with HRT 8 hour

Figure 42 - Influent and effluent SS, VFA with HRT 8hour

Figure 43 - Removal efficiency COD with HRT 8 hour

Figure 44 - Removal efficiency lipid with HRT 8hour

In an attempt to mitigate floating sludge, a stirring device was installed in the reactor. Due to the effect of the stirring force, the film layer on the granular sludge was separated and the sludge settleability became very good. When operating this device, a lot of settled deposit in reactor was washed out in the effluent.

The reactor was operated at HRT 10 hour with an organic loading rate (OLR) of 4.8 g COD/l.day, and influent was kept constant around COD 2000 mg/l. One part of the sludge was still floating on the top of reactor, despite that the stirring device had been running. Treatment efficiency was very low and the regime of HRT 6 h could not be carried out. Figure 46 shows the floating sludge phenomenon in the reactor.

From the results presented in Figure 45, it is clear that treatment efficiency  (E%) is the highest at HRT 12 hour and decreased at 8 hour. It is clear that HRT affects treatment efficiency.  Figure 45 presents the treatment efficiency of CODt, CODss and CODd  with change of HRT.

Figure 45 - Treatment efficiency change with HRT (and loading rate)

Figure 46 - Floating sludge in the reactor at HRT 8h

##### Maximum specific methanogenic activity of the granular sludge

The assessed values for TSS, VSS and ash can be found in part 3.1.1 of the materials and methods section. The SMA of sludge was calculated from the linear increase of pressure or the decrease of the substrate concentration. The VSS content was 9.95% and SMAaverage of granular sludge from Nedalco was 1.25 g COD/g VSS.day at start up of the reactor. SMA slightly decreased during the changes in operation regime of 12, 10, 8 hour corresponding to times of 38, 66 and 78 days. The value of SMA ranged from 0.84, 0.84, and 0.83 g COD/g VSS.day using acetate as substrate and 0.99, 0.94, and 0.91 using VFA as substrate.

Figure 47 - Results of SMA for initial sludge, R1, R2: duplicate experiment bottles

Figure 48 - Results of SMA after 38 days, R1, R2, R3: triplicate experiment bottles

Figure 49 - Results of SMA after 66 days, R1, R2, R3: triplicate experiment bottles

Figure 50 - Results of SMA after 78 days, R1, R2, R3: triplicate experiment bottles

### Membrane treatment results

#### UF results

UF membrane choice was performed on the base of previous experimental results. Membrane labelled MW, produced by Osmonics Inc. was selected. Investigation was carried out on pilot scale.

##### Pilot scale UF on CBL effluent

###### Pi. Sc. characterization of CBL/UF

Flow rates at different pressure and temperature values:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 1.4 | 39 |
| 1.9 | 48 |
| 2.3 | 56 |
| 2.8 | 64 |

###### Pi. Sc. complete recirculation test of CBL/UF

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 17 | 31 | 33 |
| 20 | 20 | 18 | 19 |
| 40 | 21 | 17 | 18 |
| 60 | 21 | 16 | 16 |

|  | Feed | permeate 0' | permeate 60' |
| --- | --- | --- | --- |
| pH | 8.5 | 8.7 | 8.8 |
| Conductivity [S·cm-1] | 1670 | 1496 | 1458 |
| Abs  = 426 nm | 0.022 | 0.014 | 0.008 |
| Abs  = 558 nm | 0.010 | 0.006 | 0.002 |
| Abs  = 660 nm | 0.009 | 0.006 | 0.004 |
| Abs  = 436 nm | 0.019 | 0.013 | 0.007 |
| Abs  = 525 nm | 0.010 | 0.008 | 0.003 |
| Abs  = 620 nm | 0.009 | 0.006 | 0.004 |
| TOC [mg · l-1] | 401 | 211 | 195 |
| TC [mg · l-1] | 500 | 315 | 288 |
| IC [mg · l-1] | 99 | 104 | 93 |

###### Concentration effect test of CBL/UF

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 21 | 19 | 20 |
| 40 | 22 | 15 | 15 |
| 80 | 23 | 13 | 13 |

|  | Feed | perm. 0% | perm. 40% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- |
| pH | 8.5 | 8.8 | 8.8 | 8.9 | 8.9 |
| Conductivity [S·cm-1] | 1670 | 1458 | 1518 | 1679 | 2020 |
| TOC [mg · l-1] | 401 | 195 | 221 | 278 | 799 |
| TC [mg · l-1] | 500 | 288 | 317 | 382 | 900 |
| IC [mg · l-1] | 99 | 93 | 96 | 104 | 101 |
| Abs  = 426 nm | 0.022 | 0.008 | 0.015 | 0.013 | 0.104 |
| Abs  = 558 nm | 0.01 | 0.002 | 0.008 | 0.006 | 0.057 |
| Abs  = 660 nm | 0.009 | 0.004 | 0.007 | 0.01 | 0.049 |
| Abs  = 436 nm | 0.019 | 0.007 | 0.013 | 0.011 | 0.096 |
| Abs  = 525 nm | 0.01 | 0.003 | 0.01 | 0.006 | 0.06 |
| Abs  = 620 nm | 0.009 | 0.004 | 0.007 | 0.009 | 0.054 |
| SST [mg · l-1] | 300 | - | - | - | 680 |

###### Second characterization of CBL/UF

Flow rates in the second characterization and comparison between first and second characterization:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 1.4 | 36 |
| 1.9 | 46 |
| 2.3 | 52 |
| 2.8 | 61 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 2.1 | 52 | 49 | 6% |

###### Conclusions of CBL/UF

The effluent shows very low affinity with the membrane evidenced with the high decrease in flow rate due to colloids presents in the effluent.

Rematkable decrease is observable at increasing concentrations in the feed.

Comparing first and second characterization, a minor loss occurs but taking into account the low volume filtered the loss is significant.

The quality of the permeate does not allow for reuse hypothesys, also due to low removals generally performed.

Comparison among flow rates measured in all the pilot scale trials.

Comparison among flow rates measured in all the pilot scale trials

|  | Feed | Permeate UF | Abatement % |
| --- | --- | --- | --- |
| pH | 8.5 |  | - |
| Conductivity [S·cm-1] | 1670 | 1552 | 7% |
| TOC [mg · l-1] | 401 | 231 | 42% |
| TC [mg · l-1] | 500 | 329 | 34% |
| IC [mg · l-1] | 99 | 98 | 1% |
| Abs  = 426 nm | 0.022 | 0.012 | 45% |
| Abs  = 558 nm | 0.01 | 0.005 | 47% |
| Abs  = 460 nm | 0.009 | 0.007 | 22% |
| Abs  = 436 nm | 0.019 | 0.010 | 46% |
| Abs  = 525 nm | 0.01 | 0.006 | 37% |
| Abs  = 620 nm | 0.009 | 0.007 | 26% |
| SST (mg l-1) | 300 | - | >99% |

The permeate effluent from ultrafiltration is submitted to nanofiltration as described in § 4.3.2.2.1

#### UF+NF results

The choice of the membrane to be used for the treatment was not performed on bench scale; the model Dlwas selected for its higher flows evidenced on similar effluents.

##### Pilot scale NF on CBL effluent after UF

###### Pi. Sc. characterization of CBL/NF

Flow rates at different pressure values:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 6 | 21 |
| 6.9 | 23 |
| 9 | 29 |

###### Pi. Sc. complete recirculation test of CBL/NF

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 20 | 16 | 18 |
| 20 | 23 | 19 | 20 |
| 40 | 24 | 19 | 19 |
| 60 | 25 | 19 | 19 |

|  | Feed | permeate 0' | permeate 60' |
| --- | --- | --- | --- |
| pH | 9.2 | 9.7 | 9.3 |
| Conductivity [S·cm-1] | 1552 | 363 | 379 |
| Abs  = 426 nm | 0.010 | 0.004 | 0.002 |
| Abs  = 558 nm | 0.010 | 0.003 | 0.000 |
| Abs  = 660 nm | 0.012 | 0.006 | 0.006 |
| Abs  = 436 nm | 0.009 | 0.003 | 0.003 |
| Abs  = 525 nm | 0.003 | 0.002 | 0.001 |
| Abs  = 620 nm | 0.008 | 0.006 | 0.004 |
| TOC [mg · l-1] | 229 | 24 | 37 |
| TC [mg · l-1] | 322 | 26 | 39 |
| IC [mg · l-1] | 93 | 2 | 2 |

###### Concentration effect test of CBL/NF

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 25 | 19 | 19 |
| 30 | 25 | 19 | 19 |
| 60 | 25 | 18 | 18 |

|  | Feed | perm. 0% | perm. 30% | perm. 60% | Conc. |
| --- | --- | --- | --- | --- | --- |
| pH | 9.2 | 9.3 | 8.4 | 8.5 | 9.2 |
| Conductivity [S·cm-1] | 1552 | 379 | 500 | 782 | 2859 |
| TOC [mg · l-1] | 229 | 37 | 18 | 29 | 540 |
| TC [mg · l-1] | 321 | 39 | 52 | 86 | 716 |
| IC [mg · l-1] | 93 | 2 | 33 | 57 | 175 |
| Abs  = 426 nm | 0.011 | 0.002 | 0.003 | 0.002 | 0.016 |
| Abs  = 558 nm | 0.006 | 0.000 | 0.000 | 0.000 | 0.008 |
| Abs  = 660 nm | 0.008 | 0.005 | 0.003 | 0.002 | 0.007 |
| Abs  = 436 nm | 0.010 | 0.003 | 0.003 | 0.002 | 0.013 |
| Abs  = 525 nm | 0.004 | 0.001 | 0.000 | 0.001 | 0.007 |
| Abs  = 620 nm | 0.008 | 0.004 | 0.003 | 0.001 | 0.008 |

###### Second characterization of CBL/NF

Flow rates in the second characterization and comparison among first, second and after washing characterization:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 6 | 19 |
| 6.9 | 22 |
| 9 | 29 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 6.9 | 23 | 22 | 4% |

###### Conclusions of CBL/NF

The loss in flow rate passing from pure water to CBL effluent is acceptable.

Low further loss is observableat increasing concentrations.

With the second characterization there is a good recovery of flow rate.

The quality of the permeate is very good (see reuse tests § 4.3.5.) thanks to the high removals.

Comparison among flow rates measured in all the pilot scale trials:

Quality of the aver. permeate and percentage abatement:

|  | Feed | Permeate NF | Abatement % |
| --- | --- | --- | --- |
| pH | 9.2 | 8.7 |  |
| Conductivity [S·cm-1] | 1552 | 554 | 64% |
| TOC [mg · l-1] | 229 | 28 | 88% |
| TC [mg · l-1] | 321 | 59 | 82% |
| IC [mg · l-1] | 93 | 31 | 67% |
| Abs  = 426 nm | 0.011 | 0.002 | 79% |
| Abs  = 558 nm | 0.006 | 0.000 | >99% |
| Abs  = 460 nm | 0.008 | 0.003 | 58% |
| Abs  = 436 nm | 0.010 | 0.003 | 73% |
| Abs  = 525 nm | 0.004 | 0.001 | 83% |
| Abs  = 620 nm | 0.008 | 0.003 | 67% |

Overall removal efficiency of the train UF + NF, obtained combining the results of the single treatments:

|  | Abatement % UF | Abatement % NF | Overall Efficiency % |
| --- | --- | --- | --- |
| pH |  |  |  |
| Conductivity [S·cm-1] | 7% | 64% | 67% |
| TOC [mg · l-1] | 42% | 88% | 93% |
| TC [mg · l-1] | 34% | 82% | 88% |
| IC [mg · l-1] | 1% | 67% | 67% |
| Abs  = 426 nm | 45% | 79% | 88% |
| Abs  = 558 nm | 47% | >99% | >99% |
| Abs  = 460 nm | 22% | 58% | 68% |
| Abs  = 436 nm | 46% | 73% | 85% |
| Abs  = 525 nm | 37% | 83% | 89% |
| Abs  = 620 nm | 26% | 67% | 75% |
| SST (mg l-1) | >99% | - | >99% |

### Technical - economical feasibility

In the following paragraph the technical – economical aspects related to the treatment and reuse of the effluents are presented, independently from the considerations on permeates reusability exposed in the previous paragraphs.

In the table below, for all the treatments tested on cotton bleaching, the values of three flow indexes are reported as resulted from the experimental runs. I1 describes the affinity membrane – effluent, I2 the reduction of permeate flow at increased feed concentration and I3 is an estimation of the hours of operation before washing is required.

Refer to § 3.2.3.4. to have a description of how the indexes are calculated and their influence on the economical evaluations.

In the following tables and graphs all the details of the economical evaluations are reported for each effluent and treatment tested, in § 3.2.3.4. the method applied is explained with the assumptions behind it.

It can be noted that:

- UF treatment has resulted in bad indexes values and it ends up in high costs for this kind of treatment.

- UF+NF treatment costs are not so high due to the good NF treatability of ultrafiltered effluent.  .

#### Cost estimation UF/CBL

#### Cost estimation UF+NF/CBL

### Reuse tests results

#### Reuse of bleaching permeate for cotton bleaching

##### Degree of polymerisation (DP)

The measurement of DP has been done in double, i.e. series 1 and 2.

|  | % permeate | polymerisation degree |
| --- | --- | --- |
| SERIES 1 | 0% | 1568,95 |
|  | 100% | 1744,72 |
|  | 75% | 1713,86 |
| SERIES 2 | 0% | 1724,23 |
|  | 100% | 1708,53 |
|  | 75% | 1780,35 |

All DP values are between 1500 and 2000 which is acceptable for bleached cotton. Above this, no differences are seen between the reference treatment and the bleaching with reused permeate.

##### Degree of whiteness

The degree of whiteness has been measured in double, i.e. series 1 and 2.

|  | % permeate | degree of whiteness |
| --- | --- | --- |
| SERIES 1 | 0% | 48,876 |
|  | 100% | 48,127 |
|  | 75% | 48,177 |
| SERIES 2 | 0% | 47,917 |
|  | 100% | 50,077 |
|  | 75% | 48,698 |

The higher the value, the more white is the bleached sample. The measured degree of whiteness is acceptable and the differences are less than 5 units.

##### Conclusions: reuse of permeate for bleaching cotton

Based on the measurements of DP and the degree of whiteness, the bleached cotton has the same quality whether it is bleached with 100% fresh process water or with reused bleaching permeate (both 100% and 75% permeate).

#### Reuse of bleaching permeate for direct dyeing of cotton

The direct dyeing of the bleached cotton has been done in double, i.e. series 1 and 2.

##### Colour differences

|  | % permeate |  | delta E (CMC2:1) | delta E (CMC2:1) |
| --- | --- | --- | --- | --- |
|  | bleached | dyed |  |  |
| SERIES 1 | 0% | 0% | reference | 0,61 |
|  |  | 75% | 0,19 | 0,65 |
|  | 100% | 0% | 0,15 | 0,54 |
|  |  | 75% | 0,17 | 0,45 |
|  | 75% | 0% | 0,42 | 0,19 |
|  |  | 75% | 0,32 | 0,37 |
| SERIES 2 | 0% | 0% | 0,60 | reference |
|  |  | 75% | 0,35 | 0,28 |
|  | 100% | 0% | 0,46 | 0,16 |
|  |  | 75% | 0,37 | 0,25 |
|  | 75% | 0% | 0,23 | 0,38 |
|  |  | 75% | 0,43 | 0,27 |

For each series of treatments the fabric which has been bleached and dyed with 100% fresh process water has been taken as the reference to calculate the difference in colour. All values of delta E (colour difference) are below 0.8, which means that no significant changes in colour shade can be measured. Also visually no differences were observed.

Both series of treatments have also been compared to one another, but also in this case no significant differences could be remarked.

##### Colour fastness to washing

| bleached with x% permeate | 0% |  | 100% |  | 75% |  |
| --- | --- | --- | --- | --- | --- | --- |
| dyed with x% permeate | 0% | 75% | 0% | 75% | 0% | 75% |
| change of shade |  |  |  |  |  |  |
| SERIES 1 | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 |
| SERIES 2 | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 |
| staining |  |  |  |  |  |  |
| SERIES 1 |  |  |  |  |  |  |
| wool | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 |
| cotton | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 |
| SERIES 2 |  |  |  |  |  |  |
| wool | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 |
| cotton | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 |

All values are good to very good and no differences higher than 0.5 unit are noticed.

##### Colour fastness to rubbing

| bleached with x% permeate | 0% |  | 100% |  | 75% |  |
| --- | --- | --- | --- | --- | --- | --- |
| dyed with x% permeate | 0% | 75% | 0% | 75% | 0% | 75% |
| change of shade |  |  |  |  |  |  |
| SERIES 1 |  |  |  |  |  |  |
| dry | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 |
| wet | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 |
| SERIES 2 |  |  |  |  |  |  |
| dry | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 |
| wet | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 |
| staining |  |  |  |  |  |  |
| SERIES 1 |  |  |  |  |  |  |
| dry | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 |
| wet | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 |
| SERIES 2 |  |  |  |  |  |  |
| dry | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 |
| wet | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 |

All values are good to very good and no differences higher than 0.5 unit are noticed.

##### Conclusions: reuse of permeate for bleaching and direct dyeing of cotton

The waterquality of the bleaching permeate is good enough to be reused for both bleaching and direct dyeing of cotton. No adaptations to the water quality are needed.

In the performed series of tests the reuse cycle is only been done once. The waste water of bleaching is treated via membrane filtration and reused for both bleaching and direct dyeing. The waste water of these treatments has not been treated and tested for reuse. It is to be expected that several reuse cycles will generate a higher concentration of certain chemicals in the permeate. To prevent this increase in concentration it is better to mix the permeate with fresh process water. In any case extra fresh process water is needed since part of the water is taken up by the fabric and is lost by evaporation.

## Silk polymer charge

In the present chapter, discussion and results of the experimental activities carried out on the silk polymer charge (SPC) effluents is reported: after the laboratory test to select the proper membrane, two UF membrane were tested on pilot scale. Both the ultrafiltrated effluents were treated on NF on pilot scale

### Membrane treatment results

#### UF results

##### Bench scale UF on SPC effluent

###### Characterization of SPC/UF

Flow rate measurements at 6 bar pressure for three membranes at constant temperature (25 °C):

| P |  | ER |  |  |  | PW |  |  |  |  | GK |  |  |  |  | GH |  |  |  |  | MW |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | T (°C) |  | Q (l h-1 m-2) |  | T (°C) |  | Q (l h-1 m-2) |  |  | T (°C) |  | Q (l h-1 m-2) |  |  | T (°C) |  | Q (l h-1 m-2) |  |  | Q (l h-1) |  | Q (l h-1 m-2) |
| 1 |  |  |  |  |  | 26 |  | 228 |  |  |  |  |  |  |  |  |  |  |  | 25 |  |  | 290 |  |
| 1.5 |  |  |  |  |  | 26 |  | 332 |  |  |  |  |  |  |  |  |  |  |  | 25 |  |  | 415 |  |
| 2 |  | 27 |  | 153 |  | 26 |  | 430 |  | 27 |  |  | 13 |  |  |  |  |  |  | 25 |  |  | 553 |  |
| 2.5 |  | 26 |  | 197 |  | 26 |  | 528 |  | 27 |  |  | 18 |  |  |  |  |  |  | 25 |  |  | 726 |  |
| 3 |  | 26 |  | 235 |  |  |  |  |  | 26 |  |  | 20 |  |  |  |  |  |  |  |  |  |  |  |
| 3.5 |  | 25 |  | 264 |  |  |  |  |  | 25 |  |  | 22 |  |  |  |  |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.5 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 28 |  |  | 15 |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 27 |  |  | 16 |  |  |  |  |  |  |
| 5.5 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 25 |  |  | 16 |  |  |  |  |  |  |

GK and GH were escluded form further investigation due to the low fluxes measured during the characterization.

###### Complete recirculation test of SPC/UF

Flow rate decrease passing to real effluent filtration:

| Membrane | P (bar) | T (°C) | QT [ l · h-1· m-2 ] | Flow rate decrease [%] |
| --- | --- | --- | --- | --- |
| ER | 3.4 | 33 | 60 | 79 |
| MW | 2.1 | 29 | 71 | 88 |
| PW | 2.1 | 20 | 38 | 91 |

K=0.008

Permeates quality:

|  | Feed | ER | MW | PW |
| --- | --- | --- | --- | --- |
| pH | 3.5 | 3.4 | 3.5 | 3.3 |
| Conductivity [S·cm-1] | 2440 | 2390 | 2300 | 2400 |
| Turbidity [NTU] | 1.2 | 0.2 | 0.4 | <0.1 |
| SST (mg l-1) | 21 | - | - | - |
| Abs  = 426 nm | 0.006 | 0.000 | 0.001 | 0.000 |
| Abs  = 558 nm | 0.005 | 0.000 | 0.003 | 0.005 |
| Abs  = 660 nm | 0.001 | 0.002 | 0.003 | 0.002 |
| TOC [mg · l-1] | 5699 | 1093 | 1095 | 853 |
| TC [mg · l-1] | 5729 | 1098 | 1106 | 865 |
| IC [mg · l-1] | 30 | 5 | 11 | 12 |

###### Choice of the membrane for the pilot scale

It was not possibile to make a clear choice between MW e PW because is sensibly higher in flow, the second gives better removal. Both the membrane were tested on pilot scale.

##### Pilot scale UF (membrane MW) on SPC effluent

###### Pi. Sc. characterization of SPC/UF (membrane MW)

Flow rates at different pressure and 30 °C temperature values:

| p [ bar ] | Q30 [ l · h-1] |
| --- | --- |
| 1.4 | 45 |
| 1.9 | 52 |
| 2.3 | 59 |
| 2.8 | 68 |

###### Pi. Sc. complete recirculation test of SPC/UF (membrane MW)

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 21 | 37 | 38 |
| 15 | 24 | 33 | 33 |
| 30 | 27 | 33 | 32 |
| 45 | 30 | 36 | 35 |
| 60 | 32 | 37 | 35 |

|  | Feed | Permeate 0’ | Permeate 60’ |
| --- | --- | --- | --- |
| pH | 3.5 | 3.3 | 3.2 |
| Conductivity [S·cm-1] | 2440 | 2160 | 2160 |
| Turbidity [NTU] | 1.2 | 0.4 | 0.2 |
| SST (mg l-1) | 21 | - | - |
| Abs  = 426 nm | 0.006 | 0.000 | 0.002 |
| Abs  = 558 nm | 0.005 | 0.002 | 0.004 |
| Abs  = 660 nm | 0.001 | 0.000 | 0.002 |
| TOC [mg · l-1] | 5699 | 2804 | 2299 |
| TC [mg · l-1] | 5729 | 2837 | 2304 |
| IC [mg · l-1] | 30 | 33 | 5 |

###### Concentration effect test of SPC/UF (membrane MW)

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 32 | 39 | 37 |
| 20 | 33 | 40 | 38 |
| 40 | 34 | 40 | 37 |
| 60 | 35 | 40 | 37 |
| 80 | 37 | 38 | 35 |

|  | Feed | perm. 0% | perm. 20% | perm. 40% | perm. 60% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 3.5 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 |
| Conductivity [S·cm-1] | 2440 | 2160 | 2340 | 2350 | 2370 | 2390 | 2370 |
| Turbidity [NTU] | 1.2 | 0.3 | 0.2 | 0.5 | 0.4 | 0.5 | 2.2 |
| SST (mg l-1) | 21 |  |  |  |  |  | 58 |
| Abs  = 426 nm | 0.006 | 0.001 | 0.000 | 0.000 | 0.000 | 0.000 | 0.003 |
| Abs  = 558 nm | 0.005 | 0.003 | 0.000 | 0.002 | 0.001 | 0.004 | 0.004 |
| Abs  = 660 nm | 0.001 | 0.001 | 0.000 | 0.000 | 0.000 | 0.003 | 0.002 |
| TOC [mg · l-1] | 5699 | 2552 | 2581 | 2812 | 3016 | 3594 | 12945 |
| TC [mg · l-1] | 5729 | 2571 | 2584 | 2816 | 3018 | 3597 | 12947 |
| IC [mg · l-1] | 30 | 19 | 3 | 4 | 2 | 3 | 2 |

♦ TOC in the feed

■ TOC in the permeate

###### Second characterization of SPC/UF (membrane MW)

Flow rates in the second characterization and comparison between first and second characterization:

| p [ bar ] | Q30 [ l · h-1] |
| --- | --- |
| 1.4 | 39 |
| 1.9 | 46 |
| 2.3 | 51 |
| 2.8 | 59 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 2.1 | 53 | 47 | 11 |

###### Conclusions of SPC/UF (membrane MW)

The ultrafiltration of real effluent compared to the value obtained with water filtration shows a significant decrease in flow rate.

The concentration effect test showed that the flow rate stays almost constant. During the second characterization, a high loss of flow rate occurs due to material clogging.

Despite the good removals obtained for all the pollutants, the quality of the utrafiltered effluent is clearly non acceptable for reusing in textile processes.

Comparison among flow rates measured in all the pilot scale trials:

|  | Feed | Permeate UF | Abatement % |
| --- | --- | --- | --- |
| pH | 3.5 | 3.3 |  |
| Conductivity [S·cm-1] | 2440 | 2322 | 5% |
| Turbidity [NTU] | 1.2 | 0.4 | 70% |
| SST (mg l-1) | 21 | - | >99% |
| Abs  = 426 nm | 0.006 | 0.000 | 97% |
| Abs  = 558 nm | 0.005 | 0.002 | 60% |
| Abs  = 660 nm | 0.001 | 0.001 | 20% |
| TOC [mg · l-1] | 5699 | 2911.0 | 49% |
| TC [mg · l-1] | 5729 | 2917.0 | 49% |
| IC [mg · l-1] | 30 | 6.0 | 80% |

The permeate effluent from ultrafiltration is submitted to nanofiltration as described in § 4.4.1.2.2.

##### Pilot scale UF (membrane PW) on SPC effluent

###### Pi. Sc. characterization of SPC/UF (membrane PW)

Flow rates at different pressure and 29 °C temperature values:

| p [ bar ] | Q29 [ l · h-1] |
| --- | --- |
| 1.4 | 20 |
| 1.9 | 25 |
| 2.3 | 32 |
| 2.8 | 38 |

###### Pi. Sc. complete recirculation test of SPC/UF (membrane PW)

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 29 | 17 | 17 |
| 15 | 31 | 16 | 15 |
| 30 | 33 | 17 | 16 |
| 45 | 34 | 17 | 16 |
| 60 | 35 | 18 | 17 |

|  | Feed | Permeate 0’ | Permeate 60’ |
| --- | --- | --- | --- |
| pH | 3.4 | 3.5 | 3.4 |
| Conductivity [S·cm-1] | 2460 | 2040 | 2340 |
| Turbidity [NTU] | 1.2 | 0.2 | 0.25 |
| SST (mg l-1) | 45 | - | - |
| Abs  = 426 nm | 0.004 | 0.000 | 0.001 |
| Abs  = 558 nm | 0.004 | 0.001 | 0.002 |
| Abs  = 660 nm | 0.000 | 0.000 | 0.000 |
| TOC [mg · l-1] | 5576 | 714 | 963 |
| TC [mg · l-1] | 5585 | 727 | 968 |
| IC [mg · l-1] | 9 | 13 | 5 |

###### Concentration effect test of SPC/UF (membrane PW)

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 30 | 16 | 15 |
| 20 | 32 | 15 | 14 |
| 40 | 35 | 15 | 14 |
| 60 | 37 | 15 | 13 |
| 80 | 39 | 15 | 13 |

|  | Feed | perm. 0% | perm. 20% | perm. 40% | perm. 60% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 3.5 | 3.5 | 3.4 | 3.5 | 3.5 | 3.4 | 3.4 |
| Conductivity [S·cm-1] | 2440 | 2190 | 2340 | 2390 | 2380 | 2370 | 2460 |
| Turbidity [NTU] | 1.2 | 0.2 | 0.25-0.68 | 0.2 | 0.2 | 0.3 | 2.4 |
| SST (mg l-1) | 21 | - | - | - | - | - | 59 |
| Abs  = 426 nm | 0.006 | 0.001 | 0.005 | 0.003 | 0.005 | 0.003 | 0.005 |
| Abs  = 558 nm | 0.005 | 0.002 | 0.004 | 0.004 | 0.004 | 0.002 | 0.002 |
| Abs  = 660 nm | 0.001 | 0.000 | 0.003 | 0.000 | 0.002 | 0.000 | 0.000 |
| TOC [mg · l-1] | 5699 | 839 | 1139 | 1208 | 1294 | 1504 | 14356 |
| TC [mg · l-1] | 5729 | 848 | 1141 | 1210 | 1296 | 1508 | 14358 |
| IC [mg · l-1] | 30 | 9 | 2 | 2 | 2 | 4 | 2 |

♦ TOC in the feed

■ TOC in the permeate

###### Second characterization of SPC/UF (membrane PW)

Flow rates in the second characterization and comparison between first and second characterization:

| p [ bar ] | Q30 [ l · h-1] |
| --- | --- |
| 1.4 | 12 |
| 1.9 | 14 |
| 2.3 | 17 |
| 2.8 | 20 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 2.1 | 28 | 15 | 46 |

###### Conclusions of SPC/UF (membrane PW)

When compared with UF results given by MW, membrane PW is sensibly worse in terms of affinity with the real effluent and flow rates (expecially the loss occurred during the second characterization), while the removals and the permeate quality is higher.

Comparison among flow rates measured in all the pilot scale trials:

Quality of the aver. permeate and percentage abatement:

|  | Feed | Permeate UF | Abatement % |
| --- | --- | --- | --- |
| pH | 3.5 | 3.4 | - |
| Conductivity [S·cm-1] | 2440 | 2334 | 4% |
| Turbidity [NTU] | 1.2 | 0.2 | 79% |
| SST (mg l-1) | 21 | 16 | 24% |
| Abs  = 426 nm | 0.006 | 0.003 | 43% |
| Abs  = 558 nm | 0.005 | 0.003 | 36% |
| Abs  = 660 nm | 0.001 | 0.001 | - |
| TOC [mg · l-1] | 5699 | 1196.8 | 79% |
| TC [mg · l-1] | 5729 | 1200.7 | 79% |
| IC [mg · l-1] | 30 | 3.9 | 87% |

The permeate effluent from ultrafiltration is submitted to nanofiltration as described in §  4.4.1.2.3.

#### UF +NF results

##### Bench scale NF on SPC effluent after UF

###### Characterization of SPC/NF

Flow rate measurements at 6 bar pressure for three membranes at constant temperature (25 °C):

| P 6 bar | Membrane | T [°C] | QT [ l ·h-1·m-2 ] |
| --- | --- | --- | --- |
|  | DK | 25 | 46 |
|  | DL | 25 | 60 |
|  | HL | 25 | 60 |
|  | CK | 25 | 16 |

###### Complete recirculation test of SPC/NF

Flow rate decrease passing to real effluent filtration at 6 bar pressure:

| Membrane | T (°C) | QT [ l · h-1· m-2 ] | Flow rate decrease [%] |
| --- | --- | --- | --- |
| DK | 29 | 33 | 35 |
| DL | 33 | 35 | 53 |
| HL | 26 | 39 | 37 |
| CK | 37 | <2 | 91 |

K=0.026

Permeates quality:

|  | Feed | DK | DL | HL |
| --- | --- | --- | --- | --- |
| pH | 3.3 | 3.5 | 3.5 | 3.5 |
| Conductivity [S·cm-1] | 2220 | 1030 | 1100 | 1100 |
| Turbidity [NTU] | 0.3 | 0.1 | 0.2 | 0.2 |
| SST (mg l-1) | 16 | - | - | - |
| Abs  = 426 nm | 0.004 | 0.001 | 0.000 | 0.000 |
| Abs  = 558 nm | 0.002 | 0.001 | 0.001 | 0.000 |
| Abs  = 660 nm | 0.000 | 0.000 | 0.000 | 0.001 |
| TOC [mg · l-1] | 2181 | 505 | 512 | 502 |
| TC [mg · l-1] | 2183 | 507 | 514 | 504 |
| IC [mg · l-1] | 2 | 2 | 2 | 2 |

###### Choice of the membrane for the pilot scale

With reference to alla data, both DK and HL appeared to be equally suitable for pilot scale investigation. DK was selected just in order to compare results with previous experimentals.

##### Pilot scale NF on SPC effluent after UF (MW)

###### Pi. Sc. characterization of SPC/NF on UF (MW) effluent

Flow rates at different pressure values:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 6 | 14 |
| 6.9 | 17 |
| 9 | 23 |

###### Pi. Sc. complete recirculation test of SPC/NF on UF (MW) effluent

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 23 | 12 | 13 |
| 15 | 27 | 15 | 14 |
| 30 | 29 | 6 | 14 |
| 45 | 31 | 16 | 14 |
| 60 | 32 | 18 | 14 |

|  | Feed | permeate 0' | permeate 60' |
| --- | --- | --- | --- |
| pH | 3.6 | 3.7 | 3.8 |
| Conductivity [S·cm-1] | 2220 | 890 | 980 |
| Turbidity [NTU] | 0.4 | 0.2 | 0.4 |
| SST (mg l-1) | - | - | - |
| Abs  = 436 nm | 0.005 | 0.003 | 0.006 |
| Abs  = 525 nm | 0.003 | 0.004 | 0.006 |
| Abs  = 620 nm | 0.004 | 0.003 | 0.004 |
| TOC [mg · l-1] | 2874 | 416 | 465 |
| TC [mg · l-1] | 2876 | 421 | 467 |
| IC [mg · l-1] | 2 | 5 | 2 |

###### Concentration effect test of of SPC/NF on UF (MW) effluent

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 33 | 18 | 14 |
| 20 | 35 | 19 | 14 |
| 40 | 37 | 20 | 14 |
| 60 | 43 | 21 | 13 |
| 80 | 46 | 19 | 10 |

|  | Feed | perm. 0% | perm. 20% | perm. 40% | perm. 60% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 3.3 | 3.8 | 3.7 | 3.6 | 3.6 | 3.4 | 3.1 |
| Conductivity [S·cm-1] | 2360 | 935 | 1000 | 1040 | 1140 | 1540 | 6190 |
| Turbidity [NTU] | 0.4 | 0.3 | 0.1 | 0.1 | 0.2 | 0.3 | 1.2 |
| SST (mg l-1) | - | - | - | - | - | - | - |
| Abs  = 436 nm | 0.012 | 0.005 | 0.004 | 0.005 | 0.000 | 0.000 | 0.055 |
| Abs  = 525 nm | 0.006 | 0.005 | 0.007 | 0.003 | 0.001 | 0.002 | 0.052 |
| Abs  = 620 nm | 0.006 | 0.004 | 0.004 | 0.003 | 0.001 | 0.001 | 0.056 |
| TOC [mg · l-1] | 2921 | 441 | 467 | 467 | 473 | 468 | 11010 |
| TC [mg · l-1] | 2924 | 444 | 469 | 469 | 474 | 470 | 11013 |
| IC [mg · l-1] | 3 | 3 | 2 | 2 | 2 | 2 | 3 |

♦ TOC in the feed

■ TOC in the permeate

###### Second characterization of of SPC/NF on UF (MW) effluent

Flow rates in the second characterization and comparison among first, second and after washing characterization:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 6 | 15 |
| 6.9 | 17 |
| 9 | 23 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 6.9 | 15 | 15 | - |

###### Conclusions of of SPC/NF on UF (MW) effluent

The combination of the ultrafiltered SPC with the NF membrane shows good affinity (low decrease in flow rate with reference to the pure water filtration)

At increasing concentrations, a high loss in flow rate is observed above 60% of increased concentration while the second characterization shows a complete recovery of flow rate after simple rinsing.

The quality of the permeate is low, not acceptable for reuse tests due to the  organic content in the effluent. Nevertheless the removals performed are good.

Comparison among flow rates measured in all the pilot scale trials.

Quality of the aver. permeate and percentage abatement

|  | Feed | Permeate | Abatement % |
| --- | --- | --- | --- |
| pH | 3.3 | 3.6 | - |
| Conductivity [S·cm-1] | 2360 | 1131 | 52% |
| Turbidity [NTU] | 0.4 | 0.2 | 48% |
| SST [mg l-1] | 16 | - | >99% |
| Abs  = 436 nm | 0.012 | 0.003 | 77% |
| Abs  = 525 nm | 0.006 | 0.004 | 40% |
| Abs  = 620 nm | 0.006 | 0.003 | 57% |
| TOC [mg · l-1] | 2921 | 463 | 84% |
| TC [mg · l-1] | 2924 | 465 | 84% |
| IC [mg · l-1] | 3 | 2 | 30% |

The overall removal efficiency of the train UF + NF, obtained combining the results of the single treatments, is reported in tab. below:

|  | Abatement % UF | Abatement % NF | Overall Efficiency % |
| --- | --- | --- | --- |
| pH |  | - | - |
| Conductivity [S·cm-1] | 5% | 52% | 54% |
| Turbidity [NTU] | 70% | 48% | 84% |
| SST [mg · l-1] | 24 | 99% |  |
| Abs  = 426 nm | 97% | 77% | 99.2% |
| Abs  = 558 nm | 60% | 40% | 76% |
| Abs  = 660 nm | 20% | 57% | 65% |
| TOC [mg · l-1] | 49% | 84% | 92% |
| TC [mg · l-1] | 49% | 84% | 92% |
| IC [mg · l-1] | 80% | 30% | 86% |

##### Pilot scale NF on SPC effluent after UF (PW)

###### Pi. Sc. characterization of SPC/NF on UF (PW) effluent

Flow rates at different pressure values:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 6 | 15 |
| 6.9 | 17 |
| 9 | 23 |

###### Pi. Sc. complete recirculation test of SPC/NF on UF (PW) effluent

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 24 | 12 | 13 |
| 15 | 26 | 14 | 13 |
| 30 | 29 | 15 | 13 |
| 45 | 31 | 16 | 14 |
| 60 | 33 | 17 | 14 |

|  | Feed | permeate 0' | permeate 60' |
| --- | --- | --- | --- |
| pH | 3.5 | 3.7 | 3.6 |
| Conductivity [S·cm-1] | 2720 | 770 | 1050 |
| Turbidity [NTU] | 0.4 | 0.2 | 0.1 |
| SST (mg l-1) | - | - | - |
| Abs  = 436 nm | 0.008 | 0.004 | 0.003 |
| Abs  = 525 nm | 0.009 | 0.003 | 0.002 |
| Abs  = 620 nm | 0.005 | 0.001 | 0.000 |
| TOC [mg · l-1] | 1247 | 354 | 548 |
| TC [mg · l-1] | 1256 | 360 | 550 |
| IC [mg · l-1] | 9 | 6 | 2 |

###### Concentration effect test of of SPC/NF on UF (PW) effluent

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 31 | 16 | 13 |
| 20 | 31 | 16 | 13 |
| 40 | 31 | 16 | 13 |
| 60 | 37 | 17 | 12 |
| 80 | 29 | 12 | 10 |

|  | Feed | perm. 0% | perm. 20% | perm. 40% | perm. 60% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 3.5 | 3.6 | 3.6 | 3.6 | 3.5 | 3.4 | 2.7 |
| Conductivity [S·cm-1] | 2720 | 1100 | 1050 | 1050 | 1130 | 1180 | 7220 |
| Turbidity [NTU] | 0.4 | 0.4 | 0.1 | 0.2 | 0.3 | 0.2 | 0.4 |
| SST (mg l-1) |  |  |  |  |  |  |  |
| Abs  = 436 nm | 0.008 | 0.006 | 0.001 | 0.003 | 0.001 | 0.000 | 0.004 |
| Abs  = 525 nm | 0.009 | 0.009 | 0.004 | 0.005 | 0.004 | 0.004 | 0.003 |
| Abs  = 620 nm | 0.005 | 0.005 | 0.001 | 0.004 | 0.002 | 0.001 | 0.002 |
| TOC [mg · l-1] | 1247 | 549 | 563 | 554 | 558 | 546 | 3476 |
| TC [mg · l-1] | 1256 | 552 | 565 | 557 | 561 | 548 | 3478 |
| IC [mg · l-1] | 9 | 3 | 2 | 3 | 3 | 2 | 2 |

♦ TOC in the feed

■ TOC in the permeate

###### Second characterization of of SPC/NF on UF (PW) effluent

Flow rates in the second characterization and comparison among first, second and after washing characterization:

| p [ bar ] | Q28 [ l · h-1] |
| --- | --- |
| 6 | 12 |
| 6.9 | 15 |
| 9 | 20 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 6.9 | 16 | 14 | 12 |

###### Conclusions of of SPC/NF on UF (PW) effluent

As for the flows, no sensible difference occurred when compared with the nanofiltration of the effluent from UF with membrane MW.

Dispite the better quality of the ultrafiltered with PW, final quality of the permeate is similar in the two cases.

Comparison among flow rates measured in all the pilot scale trials.

Quality of the aver. permeate and percentage abatement

|  | Feed | Permeate | Abatement % |
| --- | --- | --- | --- |
| pH | 3.5 | 3.6 |  |
| Conductivity [S·cm-1] | 2720 | 1102 | 59% |
| Turbidity [NTU] | 0.4 | 0.2 | 47% |
| Abs  = 436 nm | 0.008 | 0.002 | 73% |
| Abs  = 525 nm | 0.009 | 0.005 | 42% |
| Abs  = 620 nm | 0.005 | 0.003 | 48% |
| TOC [mg · l-1] | 1247 | 554 | 56% |
| TC [mg · l-1] | 1256 | 557 | 56% |
| IC [mg · l-1] | 9 | 3 | 70% |

Overall removal efficiency of the train UF + NF, obtained combining the results of the single treatments:

|  | Abatement % UF | Abatement % NF | Overall Efficiency % |
| --- | --- | --- | --- |
| pH | - | - | - |
| Conductivity [S·cm-1] | 4% | 59% | 61% |
| Turbidity [NTU] | 79% | 47% | 89% |
| Abs  = 426 nm | 43% | 73% | 84.4% |
| Abs  = 558 nm | 36% | 42% | 63% |
| Abs  = 660 nm | 0% | 48% | 48% |
| TOC [mg · l-1] | 79% | 56% | 91% |
| TC [mg · l-1] | 79% | 56% | 91% |
| IC [mg · l-1] | 87% | 70% | 96% |

### Technical - economical feasibility

In the following paragraph the technical – economical aspects related to the treatment and reuse of the effluents are presented, independently from the considerations on permeates reusability exposed in the previous paragraphs.

In the table below, for all the treatments tested on silk polymer charge effluent the values of three flow indexes are reported as resulted from the experimental runs. I1 describes the affinity membrane – effluent, I2 the reduction of permeate flow at increased feed concentration and I3 is an estimation of the hours of operation before washing is required.

Refer to § 3.2.3.4. to have a description of how the indexes are calculated and their influence on the economical evaluations.

In the following tables and graphs all the details of the economical evaluations are reported for each effluent and treatment tested, in § 3.2.3.4. the method applied is explained with the assumptions behind it.

It can be noted that:

- UF and UF+NF for the effluent tested resulted in quite high treatment costs showing a low potential feasibility.  .

#### Cost estimation UF/SPC

#### Cost estimation UF+NF/SPC

## Disperse dyeing and printing (Polyester dyeing, printing, washing and  rinsing)

In the present chapter, discussion and results of the experimental activities carried out on the disperse dyeing effluents is reported. In the table below, the treatments carried out on each effluent is synthesized:

| Process Effluent | UF | NF | UF+NF | UF+RO |
| --- | --- | --- | --- | --- |
| Polyester disperse dyeing (PDD) | X |  | X | X |
| Polyester disperse dyeing rins. (PDDR) |  | X |  |  |
| Polyester printed wash (PPW) | X |  | X | X |
| Polyester disperse print (PDP) | X |  | X |  |

### Membrane treatment results

#### Direct NF results

Direct nanofiltration has been applied on PDDR effluent. The results of the tests carried out according to the methods described above, on bench scale and on pilot scale are here reported.

##### Bench scale NF on PDDR effluent

###### Characterization of PDDR/NF

Flow rate measurements at 6 bar pressure for three membranes at varying temperature and reported at 25 °C:

| P 6 bar | Membrane | T [°C] | QT [ l ·h-1·m-2 ] | k | Q25 [ l ·h-1·m-2 ] |
| --- | --- | --- | --- | --- | --- |
|  | DK | 35 | 61 | 0.028 | 46 |
|  | DL | 34 | 79 | 0.023 | 64 |
|  | HL | 34 | 85 | 0.027 | 67 |

###### Complete recirculation test of PDDR/NF

Flow rate decrease passing to real effluent filtration:

| P 6 bar | Membrane | Q25 [ l · h-1· m-2 ] | Flow rate decrease [%] |
| --- | --- | --- | --- |
|  | DK | 43 | 6 |
|  | DL | 64 | 1 |
|  | HL | 59 | 12 |

Permeates quality:

|  | Feed | DK | DL | HL |
| --- | --- | --- | --- | --- |
| pH | 7.8 | 7.6 | 7.6 | 7.6 |
| Conductivity [S·cm-1] | 198 | 36 | 45 | 27 |
| Turbidity [NTU] | 0.54 | 0.38 | 0.45 | 0.37 |
| Abs  = 426 nm | 0.004 | 0.000 | 0.003 | 0.000 |
| Abs  = 558 nm | 0.003 | 0.000 | 0.000 | 0.000 |
| Abs  = 660 nm | 0.002 | 0.001 | 0.004 | 0.002 |
| Abs  = 436 nm | 0.003 | 0.000 | 0.003 | 0.000 |
| Abs  = 525 nm | 0.002 | 0.000 | 0.000 | 0.000 |
| Abs  = 620 nm | 0.003 | 0.000 | 0.002 | 0.000 |
| TOC [mg · l-1] | 18 | 3 | 7 | 7 |
| TC [mg · l-1] | 28 | 5 | 10 | 9 |
| IC [mg · l-1] | 10 | 2 | 3 | 2 |

###### Choice of the membrane for the pilot scale

Membrane DL seems to have the best fluid-dynamic affinity for maximum flow rate and minimum decrease (almost the same) passing from deionised water to real effluent filtration. Also membrane DK has a good affinity.

On the other hand, the membrane DL shows lower performances in terms of quality of the permeate.

In this case, again, DK is chosen for further investigation.

##### Pilot scale NF on PDDR effluent

###### Pi. Sc. characterization of PDDR/NF

Flow rates at different pressure values:

| p [ bar ] | Q30 [ l · h-1] | Q33 [ l · h-1] | Q35 [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- | --- |
| 6 | 17 | 18 | 18 | 13 |
| 6.9 | 20 | 20 | 21 | 15 |
| 9 | 26 | 27 | 28 | 20 |

###### Pi. Sc. complete recirculation test of PDDR/NF

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 29 | 17 | 15 |
| 15 | 31 | 17 | 14 |
| 30 | 32 | 18 | 15 |
| 45 | 33 | 18 | 14 |
| 60 | 34 | 18 | 14 |

|  | Feed | permeate 0' | permeate 60' |
| --- | --- | --- | --- |
| pH | 8.0 | 8.3 | 7.8 |
| Conductivity [S·cm-1] | 197 | 43 | 25 |
| Turbidity [NTU] | 1.2 | 0.7 | 0.4 |
| Abs  = 426 nm | 0.005 | 0.001 | 0.002 |
| Abs  = 558 nm | 0.001 | 0.000 | 0.000 |
| Abs  = 660 nm | 0.002 | 0.000 | 0.000 |
| Abs  = 436 nm | 0.005 | 0.001 | 0.002 |
| Abs  = 525 nm | 0.005 | 0.001 | 0.002 |
| Abs  = 620 nm | 0.001 | 0.000 | 0.000 |
| TOC [mg · l-1] | 20 | 14 | 18 |
| TC [mg · l-1] | 33 | 18 | 20 |
| IC [mg · l-1] | 13 | 4 | 2 |

###### Concentration effect test of PDDR/NF

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 34 | 18 | 14 |
| 20 | 35 | 18 | 13 |
| 40 | 36 | 18 | 13 |
| 60 | 37 | 18 | 13 |
| 80 | 37 | 18 | 13 |

|  | Feed | perm. 0% | perm. 20% | perm. 40% | perm. 60% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 8.0 | 7.5 | 7.1 | 7.5 | 7.8 | 8.2 | 7.6 |
| Conductivity [S·cm-1] | 197 | 38 | 38 | 47 | 61 | 127 | 759 |
| Turbidity [NTU] | 1.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.9 | 3.4 |
| Abs  = 426 nm | 0.005 | 0.005 | 0.004 | 0.002 | 0.001 | 0.006 | 0.016 |
| Abs  = 558 nm | 0.001 | 0.001 | 0.000 | 0.000 | 0.000 | 0.003 | 0.006 |
| Abs  = 660 nm | 0.002 | 0.000 | 0.003 | 0.001 | 0.000 | 0.002 | 0.005 |
| Abs  = 436 nm | 0.005 | 0.005 | 0.005 | 0.003 | 0.001 | 0.005 | 0.015 |
| Abs  = 525 nm | 0.005 | 0.004 | 0.002 | 0.003 | 0.002 | 0.005 | 0.008 |
| Abs  = 620 nm | 0.001 | 0.000 | 0.001 | 0.001 | 0.000 | 0.002 | 0.005 |
| SST [mg · l-1] | < 5 | - | - | - | - | - | 5 |
| TOC [mg · l-1] | 20 | 13 | 15 | 16 | 17 | 19 | 35 |
| TC [mg · l-1] | 33 | 17 | 19 | 27 | 20 | 24 | 91 |
| IC [mg · l-1] | 13 | 4 | 4 | 11 | 3 | 5 | 55 |

♦ TOC in the feed

■ TOC in the permeate

###### Second characterization of PDDR/NF

Flow rates in the second characterization and comparison between first and second characterization:

| p [ bar ] | Q30 [ l · h-1] | Q33 [ l · h-1] | Q35 [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- | --- |
| 6 | 16 | 17 | 18 | 13 |
| 6.9 | 18 | 20 | 20 | 14 |
| 9 | 25 | 26 | 26 | 19 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 6 | 13 | 13 | 0 |
| 6.9 | 15 | 14 | 7 |
| 9 | 20 | 19 | 5 |

###### Conclusions of PDDR/NF

Passing from water to the real effluent nanofiltration on pilot scale, a light decrease in the flow rate is observable (15 -14 l h-1) but the value stays almost  constant during the concentration effect test at varying feed concentration.

The second characterization shows a light loss in the flow rate

The quality of the permeate is acceptable for reuse tests but the abatements cannot be calculated (organic content, colour, turbidity) due to the too low levels of the parameters in the feed.

Comparison among flow rates measured in all the pilot scale trials.

Quality of the aver. permeate and percentage abatement

|  | Feed | Permeate | Abatement % |
| --- | --- | --- | --- |
| pH | 8.0 | 7.6 | - |
| Conductivity [S·cm-1] | 197 | 62 | 68 |
| Turbidity [NTU] | 1.2 | 0.7 | 42 |
| Abs  = 426 nm | 0.005 | 0.004 | 28 |
| Abs  = 558 nm | 0.001 | 0.001 | 20 |
| Abs  = 660 nm | 0.002 | 0.001 | 40 |
| Abs  = 436 nm | 0.005 | 0.004 | 24 |
| Abs  = 525 nm | 0.005 | 0.003 | 36 |
| Abs  = 620 nm | 0.001 | 0.001 | 20 |
| TOC [mg · l-1] | < 5 | - | >99 |
| TC [mg · l-1] | 20 | 16 | 21 |
| IC [mg · l-1] | 33 | 21 | 35 |

#### UF results

UF has been tested both as single treatment and as a pre-treatment to NF and RO for the PDD, PDP and PPW effluents. Separate descriptions are reported in the following.

The membrane selection was not carried out by bench scale test. Nevertheless taking into account the effluents high clogging potential and results obtained on other pretreatment effluents, the membrane selected was the MW, having the highest permeability.

##### Pilot scale UF on PDD effluent

###### Pi. Sc. characterization of PDD/UF

Flow rates at different pressure and 28°C temperature values:

| p [ bar ] | Q28 [ l · h-1] |
| --- | --- |
| 1.4 | 43 |
| 1.9 | 50 |
| 2.3 | 58 |
| 2.8 | 68 |

###### Pi. Sc. complete recirculation test of PDD/UF

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 26.5 | 56 | 56 |
| 20 | 28 | 55 | 53 |
| 40 | 28.5 | 56 | 55 |
| 60 | 29 | 56 | 54 |

|  | Feed | Permeate* |
| --- | --- | --- |
| pH | 4.7 | 4.6 |
| Conductivity [S·cm-1] | 747 | 626 |
| Turbidity [NTU] | 4.1 | 0.1 |
| SST (mg l-1) | 2 | - |
| Abs  = 426 nm | 0.093 | 0.007 |
| Abs  = 558 nm | 0.019 | 0.006 |
| Abs  = 660 nm | 0.005 | 0.001 |
| TOC [mg · l-1] | 300 | 187 |
| TC [mg · l-1] | 310 | 191 |
| IC [mg · l-1] | 10 | 4 |

*Aver. permeate during the complete recirculation test

###### Concentration effect test of PDD/UF

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 22 | 50 | 51 |
| 20 | 24.5 | 51 | 52 |
| 40 | 26.5 | 54 | 54 |
| 60 | 29 | 54 | 53 |
| 80 | n.a. | n.a. | n.a. |

|  | Feed | perm. 0% | perm. 20% | perm. 40% | perm. 60% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 4.7 | 4.6 | 4.6 | 4.6 | 4.6 | 4.7 | 4.7 |
| Conductivity [S·cm-1] | 747 | 626 | 646 | 676 | 726 | 818 | 608 |
| Turbidity [NTU] | 4.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 18 |
| SST [mg · l-1] | 2 | - | - | - | - | - | 11 |
| Abs  = 426 nm | 0.093 | 0.007 | 0.007 | 0.007 | 0.011 | 0.019 | 0.525 |
| Abs  = 558 nm | 0.019 | 0.006 | 0.005 | 0.003 | 0.006 | 0.004 | 0.112 |
| Abs  = 660 nm | 0.005 | 0.001 | 0.000 | 0.000 | 0.000 | 0.001 | 0.035 |
| TOC [mg · l-1] | 300 | 187 | 190 | 197 | 207 | 226 | 858 |
| TC [mg · l-1] | 310 | 191 | 192 | 199 | 211 | 228 | 860 |
| IC [mg · l-1] | 10 | 4 | 2 | 2 | 4 | 2 | 2 |

♦ TOC in the feed

■ TOC in the permeate

###### Second characterization of PDD/UF

Flow rates in the second characterization and comparison between first and second characterization:

| p [ bar ] | Q28 [ l · h-1] |
| --- | --- |
| 1.4 | 42 |
| 1.9 | 50 |
| 2.3 | 58 |
| 2.8 | 66 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 2.1 | 53 | 53 | 0 |

###### Conclusions of PDD/UF

During the ultrafiltration of real effluent with complete recirculation on pilot scale, a slight flow rate increase, compared to the value obtained with pure water filtration, occurred. The reason of such strange behaviour seems to be related to an uncomplete conditioning not enabling to reach the actual maximum flux value during the first characterization.

Very good behaviour also during the concentration effect test and the second characterization.

The quality of the utrafiltered effluent is clearly non acceptable for reusing in textile processes due to low removal of organic content. On the contrary removals of colour sre good.

Comparison among flow rates measured in all the pilot scale trials

|  | Feed | Permeate UF | Abatement % |
| --- | --- | --- | --- |
| pH | 4.7 | 4.62 |  |
| Conductivity [S·cm-1] | 747 | 698.4 | 7% |
| Turbidity [NTU] | 4.1 | 0.1 | 98% |
| SST (mg l-1) | 2 | - | >99% |
| Abs  = 426 nm | 0.093 | 0.010 | 89% |
| Abs  = 558 nm | 0.019 | 0.005 | 75% |
| Abs  = 660 nm | 0.005 | 0.000 | >99% |
| TOC [mg · l-1] | 300 | 201.4 | 33% |
| TC [mg · l-1] | 310 | 204.2 | 34% |
| IC [mg · l-1] | 10 | 2.8 | 72% |

The permeate effluent from ultrafiltration is submitted to nanofiltration as described in § 4.5.1.3.1 and to RO as described in § 4.5.1.4.1.

##### Pilot scale UF on PDP effluent

###### Pi. Sc. characterization of PDP/UF

Flow rates at different pressure and temperature values:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 1.4 | 39 |
| 1.9 | 47 |
| 2.3 | 53 |
| 2.8 | 61 |

###### Pi. Sc. complete recirculation test of PDP/UF

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 20 | 41 | 43 |
| 20 | 22 | 42 | 43 |
| 40 | 22 | 42 | 43 |
| 60 | 23 | 42 | 43 |

|  | Feed | permeate 0' | permeate 60' |
| --- | --- | --- | --- |
| pH | 8.4 | 8.1 | 8.4 |
| Conductivity [S·cm-1] | 570 | 523 | 514 |
| Abs  = 426 nm | 0.005 | 0.004 | 0.005 |
| Abs  = 558 nm | 0.001 | 0.000 | 0.003 |
| Abs  = 660 nm | 0.002 | 0.004 | 0.002 |
| Abs  = 436 nm | 0.006 | 0.004 | 0.005 |
| Abs  = 525 nm | 0.002 | 0.000 | 0.002 |
| Abs  = 620 nm | 0.002 | 0.003 | 0.003 |
| TOC [mg · l-1] | 57 | 1 | 4 |
| TC [mg · l-1] | 110 | 51 | 53 |
| IC [mg · l-1] | 53 | 50 | 49 |

###### Concentration effect test of PDP/UF

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 23 | 43 | 44 |
| 40 | 24 | 41 | 41 |
| 80 | 24 | 40 | 40 |

|  | Feed | perm. 0% | perm. 40% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- |
| pH | 8.4 | 8.4 | 8.5 | 8.7 | 8.5 |
| Conductivity [S·cm-1] | 570 | 514 | 545 | 595 | 640 |
| TOC [mg · l-1] | 57 | 4 | 3 | 4 | 103 |
| TC [mg · l-1] | 110 | 53 | 54 | 59 | 160 |
| IC [mg · l-1] | 53 | 49 | 51 | 55 | 57 |
| Abs  = 426 nm | 0.005 | 0.005 | 0.005 | 0.006 | 0.014 |
| Abs  = 558 nm | 0.001 | 0.003 | 0 | 0 | 0.008 |
| Abs  = 660 nm | 0.002 | 0.002 | 0.002 | 0.002 | 0.004 |
| Abs  = 436 nm | 0.006 | 0.005 | 0.005 | 0.006 | 0.013 |
| Abs  = 525 nm | 0.002 | 0.002 | 0.001 | 0.001 | 0.007 |
| Abs  = 620 nm | 0.002 | 0.003 | 0.001 | 0.002 | 0.006 |
| SST [mg · l-1] | 2.5 |  |  |  | 0.5 |

###### Second characterization of PDP/UF

Flow rates in the second characterization and comparison between first and second characterization:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 1.4 | 35 |
| 1.9 | 43 |
| 2.3 | 50 |
| 2.8 | 58 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 2.1 | 50 | 46 | 8% |

###### Conclusions of PDP/UF

During the ultrafiltration of real effluent slight flow rate decrease, compared to the value obtained with water filtration, occurs showing quite good affinity.

The concentration effect test showed a sensible flow rate decrease at increasing concentrations of the feed.

During the second characterization a relavant loss of flow rate occurs

The quality of the permeate is very good, promising for direct reuse of the permeate (see reuse tests results § 4.5.3) thanks to the good removals performed on the organic content.

Comparison among flow rates measured in all the pilot scale trials.

Comparison among flow rates measured in all the pilot scale trials

|  | Feed | Permeate UF | Abatement % |
| --- | --- | --- | --- |
| pH | 8.4 | 8.5 | - |
| Conductivity [S·cm-1] | 570 | 551 | 3% |
| TOC [mg · l-1] | 57 | 4 | 94% |
| TC [mg · l-1] | 110 | 55 | 50% |
| IC [mg · l-1] | 53 | 52 | 3% |
| Abs  = 426 nm | 0.005 | 0.005 | n.a. |
| Abs  = 558 nm | 0.001 | 0.001 | n.a. |
| Abs  = 460 nm | 0.002 | 0.002 | n.a. |
| Abs  = 436 nm | 0.006 | 0.005 | n.a. |
| Abs  = 525 nm | 0.002 | 0.001 | n.a. |
| Abs  = 620 nm | 0.002 | 0.002 | n.a. |
| SST (mg l-1) | 2.5 |  | >99% |

The permeate effluent from ultrafiltration is submitted to nanofiltration as described in § 4.5.1.3.2.

##### Pilot scale UF on PPW effluent

###### Pi. Sc. characterization of PPW/UF

Flow rates at different pressure and 27°C temperature values:

| p [ bar ] | Q27 [ l · h-1] |
| --- | --- |
| 1.4 | 39 |
| 1.9 | 48 |
| 2.3 | 52 |
| 2.8 | 60 |

###### Pi. Sc. complete recirculation test of PPW/UF

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 25 | 42 | 42 |
| 20 | 27 | 43 | 42 |
| 40 | 31 | 41 | 39 |
| 60 | 33 | 42 | 40 |

|  | Feed | Permeate* |
| --- | --- | --- |
| pH | 10.3 | 10 |
| Conductivity [S·cm-1] | 1096 | 836 |
| Turbidity [NTU] | 126 | 1.6 |
| SST (mg l-1) | 658 | - |
| Abs  = 426 nm | 0.092 | 0.020 |
| Abs  = 558 nm | 0.023 | 0.006 |
| Abs  = 660 nm | 0.011 | 0.002 |
| TOC [mg · l-1] | 305 | 172 |
| TC [mg · l-1] | 354 | 214 |
| IC [mg · l-1] | 49 | 42 |

*Aver. Permeate during the complete recirculation test

###### Concentration effect test of PPW/UF

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 28.5 | 50 | 49 |
| 20 | 31 | 51 | 49 |
| 40 | 33 | 53 | 50 |
| 60 | 36 | 54 | 50 |
| 80 | 37.5 | 56 | 51 |

|  | Feed | perm. 0% | perm. 20% | perm. 40% | perm. 60% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 10.3 | 10 | 9.7 | 9.7 | 9.6 | 9.6 | 9.4 |
| Conductivity [S·cm-1] | 1096 | 836 | 862 | 926 | 989 | 1115 | 1329 |
| Turbidity [NTU] | 126 | 1.6 | 2.3 | 2.5 | 2.7 | 2.1 | 108 |
| SST [mg · l-1] | 658 | - | - | - | - | - | 645 |
| Abs  = 426 nm | 0.092 | 0.020 | 0.027 | 0.024 | 0.033 | 0.048 | 0.251 |
| Abs  = 558 nm | 0.023 | 0.006 | 0.011 | 0.005 | 0.005 | 0.008 | 0.044 |
| Abs  = 660 nm | 0.011 | 0.002 | 0.008 | 0.000 | 0.003 | 0.002 | 0.011 |
| TOC [mg · l-1] | 305 | 172 | 173 | 182 | 193 | 222 | 698 |
| TC [mg · l-1] | 354 | 214 | 222 | 235 | 251 | 287 | 770 |
| IC [mg · l-1] | 49 | 42 | 49 | 53 | 58 | 65 | 72 |

♦ TOC in the feed

■ TOC in the permeate

###### Second characterization of PPW/UF

Flow rates in the second characterization and comparison between first and second characterization:

| p [ bar ] | Q27 [ l · h-1] |
| --- | --- |
| 1.4 | 39 |
| 1.9 | 48 |
| 2.3 | 53 |
| 2.8 | 60 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 2.1 | 50 | 50 | 0 |

###### Conclusions of PPW/UF

A very good affinity of the effluent filtered is observable in the comparison of the flow rates obtained.

Same behaviour during the concentration effect test showing that the flow rate stays constant at increasing concentrations.

During the second characterization, no loss of flow rate occurs.

The quality of the ultrafiltered effluent is clearly non acceptable for reusing in textile processes due to the low removals obtained expecially for the organic content which stays too high in the permeate.

Comparison among flow rates measured in all the pilot scale trials

|  | Feed | Permeate UF | Abatement % |
| --- | --- | --- | --- |
| pH | 10.3 | 9.72 |  |
| Conductivity [S·cm-1] | 1096 | 945.6 | 14% |
| Turbidity [NTU] | 126 | 2.24 | 98% |
| SST (mg l-1) | 658 | - | >99% |
| Abs  = 426 nm | 0.092 | 0.0304 | 67% |
| Abs  = 558 nm | 0.023 | 0.007 | 70% |
| Abs  = 660 nm | 0.011 | 0.003 | 73% |
| TOC [mg · l-1] | 305 | 188.4 | 38% |
| TC [mg · l-1] | 354 | 241.8 | 32% |
| IC [mg · l-1] | 49 | 53.4 | -9% |

The permeate effluent from ultrafiltration is submitted to nanofiltration as described in § 4.5.1.3.3. and to RO as described in § 4.5.1.4.2.

#### UF+NF results

The choice of the membrane to be used for the treatment was not performed on bench scale; the model DK was selected for its better removal of organics and salts as evidenced on similar effluents.

##### Pilot scale NF on PDD effluent after UF

###### Pi. Sc. characterization of PDD/NF

Flow rates at different pressure values, measured at 29° C:

| p [ bar ] | Q29 [ l · h-1] |
| --- | --- |
| 6 | 15 |
| 6.9 | 18 |
| 9 | 24 |

###### Pi. Sc. complete recirculation test of PDD/NF

Flow rate vs. time and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 28 | 17 | 15 |
| 20 | 31 | 18 | 15 |
| 40 | 34 | 20 | 15 |
| 60 | 37 | 21 | 15 |

|  | Feed | Permeate* |
| --- | --- | --- |
| pH | 4.8 | 4.6 |
| Conductivity [S·cm-1] | 684 | 269 |
| Turbidity [NTU] | 0.1 | 0.1 |
| Abs  = 426 nm | 0.006 | 0.001 |
| Abs  = 558 nm | 0.000 | 0.000 |
| Abs  = 660 nm | 0.000 | 0.000 |
| TOC [mg · l-1] | 183 | 103 |
| TC [mg · l-1] | 185 | 106 |
| IC [mg · l-1] | 2 | 3 |

*Aver. Permeate during the complete recirculation test

###### Concentration effect test of PDD/NF

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 31 | 19 | 16 |
| 20 | 36 | 20 | 15 |
| 40 | 40 | 22 | 14 |
| 60 | 40 | 22 | 14 |
| 80 | 44 | 22 | 13 |

|  | Feed | perm. 0% | perm. 20% | perm. 40% | perm. 60% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 4.8 | 4.6 | 4.7 | 4.7 | 4.8 | 4.7 | 4.7 |
| Conductivity [S·cm-1] | 684 | 269 | 315 | 353 | 406 | 529 | 1663 |
| Turbidity [NTU] | 0.1 | 0.1 | 0.2 | 0.1 | 0.3 | 0 | 0.5 |
| Abs  = 426 nm | 0.006 | 0.001 | 0.002 | 0.001 | 0.002 | 0.002 | 0.026 |
| Abs  = 558 nm | 0.000 | 0.000 | 0.001 | 0.001 | 0.000 | 0.000 | 0.002 |
| Abs  = 660 nm | 0.000 | 0.000 | 0.001 | 0.000 | 0.000 | 0.000 | 0.000 |
| TOC [mg · l-1] | 183 | 103 | 114 | 126 | 137 | 161 | 365 |
| TC [mg · l-1] | 185 | 106 | 117 | 129 | 139 | 163 | 369 |
| IC [mg · l-1] | 2 | 3 | 3 | 3 | 2 | 2 | 4 |

♦ TOC in the feed

■ TOC in the permeate

###### Second characterization of PDD/NF

Flow rates in the second characterization and comparison between first and second characterization:

| p [ bar ] | Q29 [ l · h-1] |
| --- | --- |
| 6 | 15 |
| 6.9 | 18 |
| 9 | 23 |

| p [bar] | Q25 caratt. [ l · h-1] | Q25 II caratt. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 6.9 | 16 | 16 | 0 |

###### Conclusions of PDD/NF

The pilot scale investigation showed good affinity. In fact, passing from water to the real effluent a very low decrease in the flow rate.

The value of loss in flow ratecan be considered sensible during the test at increasing feed concentration.

The second characterization reveals no loss in the flow rate, which shows no clogging phenomenon.

The undifferentiated reuse of the permeate seems to be difficult due to the high value of residual DOC, for which the removal performed was not satisfactory.

Comparison among flow rates measured in all the pilot scale trials.

Quality of the aver. permeate and percentage abatement

|  | Feed | Permeate | Abatement % |
| --- | --- | --- | --- |
| pH | 4.8 | 4.7 | - |
| Conductivity [S·cm-1] | 684 | 374.4 | 45% |
| Turbidity [NTU] | 0.1 | 0.1 | n.a. |
| Abs  = 426 nm | 0.006 | 0.002 | 73% |
| Abs  = 558 nm | 0.000 | 0.000 | n.a. |
| Abs  = 660 nm | 0.000 | 0.000 | n,a, |
| TOC [mg · l-1] | 183 | 128.2 | 30% |
| TC [mg · l-1] | 185 | 130.8 | 29% |
| IC [mg · l-1] | 2 | 2.6 | -30% |

Overall removal efficiency of the train UF + NF, obtained combining the results of the single treatments:

|  | Abatement % UF | Abatement % NF | Overall Efficiency % |
| --- | --- | --- | --- |
| pH | - | - | - |
| Conductivity [S·cm-1] | 7% | 45% | 49% |
| Turbidity [NTU] | 98% | - | 98% |
| SST [mg · l-1] | >99% | - | >99% |
| Abs  = 426 nm | 89% | 73% | 97.1% |
| Abs  = 558 nm | 75% | n.a. | >75% |
| Abs  = 660 nm | 92% | n.a. | >92% |
| TOC [mg · l-1] | 33% | 30% | 53% |
| TC [mg · l-1] | 34% | 29% | 53% |
| IC [mg · l-1] | 72% | -30% | 64% |

##### Pilot scale NF on PDP effluent after UF

###### Pi. Sc. characterization of PDP/NF

Flow rates at different pressure values:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 6 | 20 |
| 6.9 | 23 |
| 9 | 31 |

###### Pi. Sc. complete recirculation test of PDP/NF

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 23 | 18 | 19 |
| 20 | 24 | 19 | 19 |
| 40 | 25 | 20 | 20 |
| 60 | 26 | 20 | 20 |

|  | Feed | permeate 0' | permeate 60' |
| --- | --- | --- | --- |
| pH | 8.5 | 7.7 | 8.2 |
| Conductivity [S·cm-1] | 551 | 175 | 182 |
| Abs  = 426 nm | 0.011 | 0.008 | 0.002 |
| Abs  = 558 nm | 0.009 | 0.009 | 0.001 |
| Abs  = 660 nm | 0.013 | 0.012 | 0.002 |
| Abs  = 436 nm | 0.013 | 0.007 | 0.002 |
| Abs  = 525 nm | 0.008 | 0.007 | 0.001 |
| Abs  = 620 nm | 0.014 | 0.016 | 0.002 |
| TOC [mg · l-1] | 5 | 5 | 4 |
| TC [mg · l-1] | 61 | 23 | 22 |
| IC [mg · l-1] | 56 | 18 | 18 |

###### Concentration effect test of PDP/NF

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 22 | 17 | 18 |
| 30 | 26 | 22 | 22 |
| 60 | 26 | 21 | 21 |

|  | Feed | perm. 0% | perm. 30% | perm. 60% | Conc. |
| --- | --- | --- | --- | --- | --- |
| pH | 8.5 | 8.2 | 8.4 | 8.4 | 8.8 |
| Conductivity [S·cm-1] | 551 | 182 | 226 | 306 | 918 |
| TOC [mg · l-1] | 5 | 4 | 4 | 3 | 1 |
| TC [mg · l-1] | 61 | 22 | 25 | 33 | 85 |
| IC [mg · l-1] | 56 | 18 | 22 | 30 | 84 |
| Abs  = 426 nm | 0.006 | 0.002 | 0.003 | 0.001 | 0.009 |
| Abs  = 558 nm | 0.002 | 0.001 | 0.001 | 0.000 | 0.004 |
| Abs  = 660 nm | 0.006 | 0.002 | 0.001 | 0.006 | 0.003 |
| Abs  = 436 nm | 0.006 | 0.002 | 0.003 | 0.002 | 0.009 |
| Abs  = 525 nm | 0.000 | 0.001 | 0.002 | 0.000 | 0.006 |
| Abs  = 620 nm | 0.006 | 0.002 | 0.001 | 0.002 | 0.004 |

###### Second characterization of PDP/NF

Flow rates in the second characterization and comparison among first, second and after washing characterization:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 6 | 21 |
| 6.9 | 24 |
| 9 | 32 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 6.9 | 23 | 24 | - |

###### Conclusions of PDP/NF

Quite good affinity is observed passing from pure water to real effluent filtration.

At increasing concentrations of the feed the behaviour stays good (flow rate seems to increase).

The second characterization confirms that non clogging phenomena occur.

The good quality of the permeate is mostly due to the good quality of the feed; the permeate improves its quality in conductivity.

Comparison among flow rates measured in all the pilot scale trials.

Quality of the aver. permeate and percentage abatement:

|  | Feed | Permeate NF | Abatement % |
| --- | --- | --- | --- |
| pH | 8.5 | 8.3 | - |
| Conductivity [S·cm-1] | 551 | 238 | 57% |
| TOC [mg · l-1] | 5 | 4 | 28% |
| TC [mg · l-1] | 61 | 27 | 56% |
| IC [mg · l-1] | 56 | 23 | 59% |
| Abs  = 426 nm | 0.006 | 0.002 | n.a. |
| Abs  = 558 nm | 0.002 | 0.001 | n.a. |
| Abs  = 460 nm | 0.006 | 0.003 | n.a. |
| Abs  = 436 nm | 0.006 | 0.003 | n.a. |
| Abs  = 525 nm | 0.000 | 0.001 | n.a. |
| Abs  = 620 nm | 0.006 | 0.002 | n.a. |

Overall removal efficiency of the train UF + NF, obtained combining the results of the single treatments:

|  | Abatement % UF | Abatement % NF | Overall Efficiency % |
| --- | --- | --- | --- |
| pH | - | - | - |
| Conductivity [S·cm-1] | 3% | 57% | 58% |
| TOC [mg · l-1] | 94% | 28% | 95% |
| TC [mg · l-1] | 50% | 56% | 78% |
| IC [mg · l-1] | 3% | 59% | 60% |
| Abs  = 426 nm | n.a. | n.a. | n.a. |
| Abs  = 558 nm | n.a. | n.a. | n.a. |
| Abs  = 460 nm | n.a. | n.a. | n.a. |
| Abs  = 436 nm | n.a. | n.a. | n.a. |
| Abs  = 525 nm | n.a. | n.a. | n.a. |
| Abs  = 620 nm | n.a. | n.a. | n.a. |
| SST (mg l-1) | >99% | - | >99% |

##### Pilot scale NF on PPW effluent after UF

###### Pi. Sc. characterization of PPW/NF

Flow rates at different pressure values, measured at 31° C:

| p [ bar ] | Q26 [ l · h-1] |
| --- | --- |
| 6 | 16 |
| 6.9 | 18 |
| 9 | 24 |

###### Pi. Sc. complete recirculation test of PPW/NF

Flow rate vs. time and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 34 | 18 | 13 |
| 20 | 36 | 18 | 13 |
| 40 | 39 | 20 | 13 |
| 60 | 42 | 21 | 13 |

|  | Feed | Permeate* |
| --- | --- | --- |
| pH | 10 | 10.3 |
| Conductivity [S·cm-1] | 956 | 198 |
| Turbidity [NTU] | 2.3 | 0.7 |
| Abs  = 426 nm | 0.032 | 0.002 |
| Abs  = 558 nm | 0.008 | 0.002 |
| Abs  = 660 nm | 0.007 | 0.004 |
| TOC [mg · l-1] | 197 | 16 |
| TC [mg · l-1] | 245 | 21 |
| IC [mg · l-1] | 48 | 5 |

*Aver. Permeate during the complete recirculation test

###### Concentration effect test of PPW/NF

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 23 | 11 | 12 |
| 20 | 30 | 15 | 13 |
| 40 | 37 | 18 | 12 |
| 60 | 43 | 20 | 12 |
| 80 | n.a. | n.a. | n.a. |

|  | Feed | perm. 0% | perm. 20% | perm. 40% | perm. 60% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 10 | 10.3 | 10 | 9.9 | 10 | 9.8 | 9.2 |
| Conductivity [S·cm-1] | 956 | 198 | 163 | 173 | 243 | 324 | 3330 |
| Turbidity [NTU] | 2.3 | 0.7 | 1.1 | 1.1 | 1.3 | 0.9 | 5.2 |
| Abs  = 426 nm | 0.032 | 0.002 | 0.003 | 0.002 | 0.016 | 0.001 | 0.123 |
| Abs  = 558 nm | 0.008 | 0.002 | 0.003 | 0.002 | 0.015 | 0.002 | 0.018 |
| Abs  = 660 nm | 0.007 | 0.004 | 0.004 | 0.003 | 0.017 | 0.005 | 0.009 |
| TOC [mg · l-1] | 197 | 16 | 15 | 19 | 24 | 28 | 828 |
| TC [mg · l-1] | 245 | 21 | 21 | 29 | 36 | 52 | 1083 |
| IC [mg · l-1] | 48 | 5 | 6 | 10 | 12 | 24 | 255 |

♦ TOC in the feed

■ TOC in the permeate

###### Second characterization of PPW/NF

Flow rates in the second characterization and comparison between first and second characterization:

| p [ bar ] | Q26 [ l · h-1] |
| --- | --- |
| 6 | 16 |
| 6.9 | 18 |
| 9 | 24 |

| p [bar] | Q25 caratt. [ l · h-1] | Q25 II caratt. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 6.9 | 15 | 15 | 0 |

###### Conclusions of PPW/NF

The affinity effluent/membrane is quite good as from the decrease of flow rate observable.

At increasing concentration of the feed the flow rate stays almost constant.

During the second characterization a complete recovery of the maximum flow rate is obtained.

The permeate seems to be suitable for reuse purpose thanks to the high abatements obtained on all the parameters.

Comparison among flow rates measured in all the pilot scale trials:

Quality of the aver. permeate and percentage abatement

|  | Feed | Permeate | Abatement % |
| --- | --- | --- | --- |
| pH | 10 | 10 |  |
| Conductivity [S·cm-1] | 956 | 220.2 | 77% |
| Turbidity [NTU] | 2.3 | 1.02 | 56% |
| Abs  = 426 nm | 0.032 | 0.005 | 85% |
| Abs  = 558 nm | 0.008 | 0.005 | 40% |
| Abs  = 660 nm | 0.007 | 0.007 | 6% |
| TOC [mg · l-1] | 197 | 20.4 | 90% |
| TC [mg · l-1] | 245 | 31.8 | 87% |
| IC [mg · l-1] | 48 | 11.4 | 76% |

Overall removal efficiency of the train UF + NF, obtained combining the results of the single treatments:

|  | Abatement % UF | Abatement % NF | Overall Efficiency % |
| --- | --- | --- | --- |
| pH | - | - | - |
| Conductivity [S·cm-1] | 14% | 77% | 80% |
| Turbidity [NTU] | 98% | 56% | 99% |
| SST [mg · l-1] | >99% | - | >99% |
| Abs  = 426 nm | 67% | 85% | 95.0% |
| Abs  = 558 nm | 70% | 40% | 82% |
| Abs  = 660 nm | 73% | 6% | 74% |
| TOC [mg · l-1] | 38% | 90% | 94% |
| TC [mg · l-1] | 32% | 87% | 91% |
| IC [mg · l-1] | -9% | 76% | 74% |

#### UF+RO results

The membrane used is SG by Osmonics, Inc. having the highest permeability among the RO membranes suitable for industrial effluents.

##### Pilot scale RO on PDD effluent after UF

###### Pi. Sc. characterization of PDD/RO

Flow rates at different pressure values, measured at 26° C:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 6 | 2.9 |
| 10 | 5.5 |
| 13.8 | 7.6 |

###### Pi. Sc. complete recirculation test of PDD/ RO

Flow rate vs. time and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 22 | 1.7 | 1.8 |
| 20 | 22 | 2.2 | 2.4 |
| 40 | 26 | 2.7 | 2.6 |
| 60 | 30 | 3.0 | 2.6 |

|  | Feed | Permeate* |
| --- | --- | --- |
| pH | 4.4 | 4 |
| Conductivity [S·cm-1] | 608 | 53 |
| Turbidity [NTU] | 0.2 | 0.1 |
| Abs  = 426 nm | 0.006 | 0.000 |
| Abs  = 558 nm | 0.001 | 0.000 |
| Abs  = 660 nm | 0.000 | 0.000 |
| TOC [mg · l-1] | 263 | 37 |
| TC [mg · l-1] | 265 | 39 |
| IC [mg · l-1] | 2 | 2 |

*Aver. Permeate during the complete recirculation test

###### Concentration effect test of PDD/ RO

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 29,5 | 2.0 | 1.8 |
| 20 | 28,5 | 2.1 | 1.9 |
| 40 | 33 | 1.7 | 1.3 |
| 60 | 32 | 1.7 | 1.4 |
| 70 | 30 | 1.8 | 1.6 |

|  | Feed | perm. 0% | perm. 20% | perm. 40% | perm. 60% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 4.4 | 4 | 4 | 4.1 | 4.2 | 4.2 | 4.4 |
| Conductivity [S·cm-1] | 608 | 53 | 55 | 53 | 73 | 87 | 1877 |
| Turbidity [NTU] | 0.2 | 0.1 | 0.4 | 0 | 0.2 | 0.1 | 4.5 |
| Abs  = 426 nm | 0.006 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.032 |
| Abs  = 558 nm | 0.001 | 0.000 | 0.000 | 0.000 | 0.001 | 0.001 | 0.013 |
| Abs  = 660 nm | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.011 |
| TOC [mg · l-1] | 263 | 37 | 34 | 34 | 50 | 66 | 841 |
| TC [mg · l-1] | 265 | 39 | 36 | 36 | 54 | 68 | 845 |
| IC [mg · l-1] | 2 | 2 | 2 | 2 | 4 | 2 | 4 |

♦ TOC in the feed

■ TOC in the permeate

###### Second characterization of PDD/ RO

Flow rates in the second characterization and comparison between first and second characterization:

| p [ bar ] | Q26 [ l · h-1] |
| --- | --- |
| 6 | 0.9 |
| 10 | 1.8 |
| 13.8 | 2.6 |

| p [bar] | Q25 caratt. [ l · h-1] | Q25 II caratt. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 13.8 | 7.4 | 2.5 | 66 |

###### Conclusions of PDD/ RO

The affinity between effluent and membrane is not good at all: the flow rate filtering real effluent is almost 30% of the flow rate obtainable with pure water.

During the concentration effect test no further loss in flow rate occurs.

The second characterization shows that the loss in flow rate is permanent, the flow rate with pure water stays low.

The quality of the permeate is good and the removals performed by the RO are high.

Comparison among flow rates measured in all the pilot scale trials:

Quality of the aver. permeate and percentage abatement:

|  | Feed | Permeate | Abatement % |
| --- | --- | --- | --- |
| pH | 4.4 | 4.1 | - |
| Conductivity [S·cm-1] | 608 | 64.2 | 89% |
| Turbidity [NTU] | 0.2 | 0.16 | 20% |
| Abs  = 426 nm | 0.006 | 0.000 | >99% |
| Abs  = 558 nm | 0.001 | 0.000 | 60% |
| Abs  = 660 nm | 0.000 | 0.000 | - |
| TOC [mg · l-1] | 263 | 44.2 | 83% |
| TC [mg · l-1] | 265 | 46.6 | 82% |
| IC [mg · l-1] | 2 | 2.4 | -20% |

Overall removal efficiency of the train UF + RO, obtained combining the results of the single treatments:

|  | Abatement % UF | Abatement % RO | Overall Efficiency % |
| --- | --- | --- | --- |
| pH | - | - | - |
| Conductivity [S·cm-1] | 7% | 89% |  |
| Turbidity [NTU] | 98% | 20 |  |
| SST [mg · l-1] | >99% | - | >99% |
| Abs  = 426 nm | 89% | n.a. | >89 |
| Abs  = 558 nm | 75% | n.a. | >75 |
| Abs  = 660 nm | n.a. | n.a. | n.a. |
| TOC [mg · l-1] | 33% | 83% | 89% |
| TC [mg · l-1] | 34% | 82% | 88% |
| IC [mg · l-1] | 72% | -20% | 66% |

##### Pilot scale RO on PPW effluent after UF

###### Pi. Sc. characterization of PPW/RO

Flow rates at different pressure values, measured at 28° C:

| p [ bar ] | Q28 [ l · h-1] |
| --- | --- |
| 6 | 2.2 |
| 10 | 3.6 |
| 13.8 | 4.7 |

###### Pi. Sc. complete recirculation test of PPW/ RO

Flow rate vs. time and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 22 | 3.3 | 3.6 |
| 30 | 26 | 4.3 | 4.2 |
| 60 | 30 | 5.1 | 4.4 |

|  | Feed | Permeate* |
| --- | --- | --- |
| pH | 10.2 | 9.8 |
| Conductivity [S·cm-1] | 998 | 90 |
| Turbidity [NTU] | 2.3 | 0.6 |
| Abs  = 426 nm | 0.032 | 0.000 |
| Abs  = 558 nm | 0.006 | 0.000 |
| Abs  = 660 nm | 0.004 | 0.000 |
| TOC [mg · l-1] | 163 | 3 |
| TC [mg · l-1] | 196 | 6 |
| IC [mg · l-1] | 33 | 3 |

*Aver. Permeate during the complete recirculation test

###### Concentration effect test of PPW/ RO

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 31.5 | 4.8 | 4.0 |
| 20 | 31 | 4.6 | 3.9 |
| 40 | 25 | 3.5 | 3.5 |
| 60 | 27.5 | 3.3 | 3.1 |
| 70 | 33 | 3.6 | 2.9 |

|  | Feed | perm. 0% | perm. 20% | perm. 40% | perm. 60% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 10.2 | 9.8 | 9.8 | 9.9 | 9.8 | 9.8 | 9.2 |
| Conductivity [S·cm-1] | 998 | 90 | 107 | 117 | 126 | 120 | 2250 |
| Turbidity [NTU] | 2.3 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 5 |
| Abs  = 426 nm | 0.032 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.070 |
| Abs  = 558 nm | 0.006 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.008 |
| Abs  = 660 nm | 0.004 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.002 |
| TOC [mg · l-1] | 163 | 3 | 2 | 3 | 3 | 3 | 426 |
| TC [mg · l-1] | 196 | 6 | 5 | 7 | 7 | 8 | 471 |
| IC [mg · l-1] | 33 | 3 | 3 | 4 | 4 | 5 | 45 |

♦ TOC in the feed

■ TOC in the permeate

###### Second characterization of PPW/ RO

Flow rates in the second characterization and comparison between first and second characterization:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 6 | 1.5 |
| 10 | 2.6 |
| 13.8 | 3.3 |

| p [bar] | Q25 caratt. [ l · h-1] | Q25 II caratt. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 13.8 | 4.3 | 3.0 | 30 |

###### Conclusions of PPW/ RO

The loss in flow rate passing from pure water to real effluent filtration is very low showing a good affinity. This is the only case in which such affinity is observable with RO membranes.

On the contrary a more sensible effect of the concentration occurs.

The original flow is not recovered during the second characterization.

The quality of the permeate is very good and the abatements high for all the parameters.

Comparison among flow rates measured in all the pilot scale trials:

Quality of the aver. permeate and percentage abatement:

|  | Feed | Permeate | Abatement % |
| --- | --- | --- | --- |
| pH | 10.2 | 9.82 | - |
| Conductivity [S·cm-1] | 998 | 112 | 89% |
| Turbidity [NTU] | 2.3 | 0.52 | 77% |
| SST [mg · l-1] | - | - | - |
| Abs  = 426 nm | 0.032 | 0.000 | >99% |
| Abs  = 558 nm | 0.006 | 0.000 | >99% |
| Abs  = 660 nm | 0.004 | 0.000 | >99% |
| TOC [mg · l-1] | 163 | 2.8 | 98% |
| TC [mg · l-1] | 196 | 6.6 | 97% |
| IC [mg · l-1] | 33 | 3.8 | 88% |

The overall removal efficiency of the train UF + NF, obtained combining the results of the single treatments, is reported in tab. below:

|  | Abatement % UF | Abatement % RO | Overall Efficiency % |
| --- | --- | --- | --- |
| pH | - | - | - |
| Conductivity [S·cm-1] | 14% | 89% | 90% |
| Turbidity [NTU] | 98% | 77% | >99% |
| SST [mg · l-1] | >99% | - | >99% |
| Abs  = 426 nm | 67% | >99% | >99% |
| Abs  = 558 nm | 70% | >99% | >99% |
| Abs  = 660 nm | 73% | >99% | >99% |
| TOC [mg · l-1] | 38% | 98% | 99% |
| TC [mg · l-1] | 32% | 97% | 98% |
| IC [mg · l-1] | -9% | 88% | 87% |

### Technical - economical feasibility

In the following paragraph the technical – economical aspects related to the treatment and reuse of the effluents are presented, independently from the considerations on permeates reusability exposed in the previous paragraphs.

In the table below, for all the treatments tested on disperse dyeing and printing effluents, the values of three flow indexes are reported as resulted from the experimental runs. I1 describes the affinity membrane – effluent, I2 the reduction of permeate flow at increased feed concentration and I3 is an estimation of the hours of operation before washing is required.

Refer to § 3.2.3.4. to have a description of how the indexes are calculated and their influence on the economical evaluations.

In the following tables and graphs all the details of the economical evaluations are reported for each effluent and treatment tested, in § 3.2.3.4. the method applied is explained with the assumptions behind it.

It can be noted that:

- UF+RO for both the effluents tested resulted in high treatment costs, also in the hypothesis of large volume of effluents to be treated, even if PPW gave good results in terms of flux indexes.

- The other treatment trains tested UF, NF and UF+NF have shown a potentially high feasibility in terms of costs.

#### Cost estimation UF/PDD

#### Cost estimation UF/PDP

#### Cost estimation UF/PPW

#### Cost estimation UF+NF/PDD

#### Cost estimation UF+NF/PDP

#### Cost estimation UF+NF/PPW

#### Cost estimation NF/PDDR

#### Cost estimation UF+RO/PDD

#### Cost estimation UF+RO/PPW

### Reuse tests results (dyeing rinsing and printing)

#### Reuse of disperse printing effluent

The permeate of disperse printing has been reused for disperse dyeing of polyester both in a light and a dark colour shade.

##### Colour differences

|  | % permeate | delta E (CMC2:1) |
| --- | --- | --- |
| reference | 0% |  |
| light | 100% | 0,68 |
| light | 75% | 0,77 |
| reference | 0% |  |
| dark | 100% | 0,38 |
| dark | 75% | 0,63 |

For each colour shade the fabric, dyed with 100% fresh process water, has been taken as the reference to calculate the difference in colour. All values of delta E (colour difference) are below 0.8, which means that no significant changes in colour shade can be measured. Also visually no differences were observed.

##### Colour fastness to washing

|  | light |  |  | dark |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| %permeate | 0% | 100% | 75% | 0% | 100% | 75% |
| change of shade | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 |
| staining |  |  |  |  |  |  |
| polyester | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 |
| cotton | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 |

All values are good to very good and no differences higher than 0.5 unit are noticed.

##### Colour fastness to rubbing

|  | light |  |  | dark |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| % permeate | 0% | 100% | 75% | 0% | 100% | 75% |
| change of shade |  |  |  |  |  |  |
| dry | 5 | 5 | 5 | 5 | 5 | 5 |
| wet | 5 | 5 | 5 | 5 | 5 | 5 |
| staining |  |  |  |  |  |  |
| dry | 5 | 5 | 5 | 5 | 5 | 5 |
| wet | 5 | 5 | 5 | 5 | 5 | 5 |

All values are very good and no differences are seen.

##### Conclusions: reuse of permeate for disperse dyeing of polyester

The waterquality of the dispers print permeate is good enough to be reused for dispers dyeing of polyester. No adaptations to the water quality are needed.

In the performed series of tests the reuse cycle is only been done once. The waste water of dispers printing is treated via membrane filtration and reused for dispers dyeing. The waste water of dispers dyeing and rinsing has not been treated and tested for reuse. It is to be expected that several reuse cycles will generate a higher concentration of certain chemicals in the permeate. To prevent this increase in concentration it is better to mix the permeate with fresh process water. In any case extra fresh process water is needed since part of the water is taken up by the fabric and is lost by evaporation.

#### Reuse of disperse dyeing effluent

The permeate of disperse dyeing has been reused for scouring and disperse dyeing of polyester both in a light and a dark colour shade.

##### Scouring efficiency

| TYPE OF TREATMENT | DEGREE OF WHITH | x | y | Y |
| --- | --- | --- | --- | --- |
| REFERENCE | 82.0 | 0.3144 | 0.3321 | 84.3 |
| REUSE | 80.0 | 0.3149 | 0.3324 | 83.2 |

The variations in the values of the degree of white in the polyester samples scoured with two water types, is irrelevant.

##### Colour differences

DYE WITH DISPERSE DYES  (TERASIL - CIBA)

| Formula: CMC 2.0:1.0 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Substratum: 100% POLYESTER |  |  |  |  |  |
| Reference: COL. GREY – DYE WITH INDUSTRIAL WATER |  |  |  |  |  |
| Sample: COL. GREY –DYE WITH TREATED WATER |  |  |  |  |  |
|  | delE | delL | delC | delH | The sample s |
| D65/10 | 0.344 | 0.297 | -0.003 | -0.175 | + clear+ green |
| A/10 | 0.324 | 0.290 | 0.086 | -0.116 | + clear |
| F11/10 | 0.322 | 0.296 | 0.032 | -0.124 | + clear |

| Formula: CMC 2.0:1.0 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Substratum: 100% POLYESTER |  |  |  |  |  |
| Reference COL. BLUE SEA – DYE WITH INDUSTRIAL WATER |  |  |  |  |  |
| Sample: COL. BLUE SEA – DYE WITH TREATED WATER |  |  |  |  |  |
|  | delE | delL | delC | delH | the sample is |
| D65/10 | 0.409 | 0.181 | 0.310 | 0.196 | + clear + pure + violet |
| A/10 | 0.320 | 0.181 | 0.258 | 0.057 | + clear + pure |
| F11/10 | 0.361 | 0.192 | 0.284 | 0.113 | + clear + pure |

The variations of tone between the samples dyed in the two types of water are within the acceptable levels of tolerance as recommended in the quality standard norm of the 2003 edition of Italian Textile Association. ( i.e.: delE=1)

##### Colour fastness to washing

grey colour:

|  | dyeING IN industrial water | dyeING IN treated water |
| --- | --- | --- |
| Degradation colour: | 4-5 | 4-5 |
| Staining on: |  |  |
| Wool | 4-5 | 4-5 |
| Acrylic | 4-5 | 4-5 |
| Polyester | 4-5 | 4-5 |
| Polyamide | 4 | 4 |
| Cotton | 4-5 | 4-5 |
| Acetate | 4-5 | 4-5 |

bleu sea colour:

|  | dye with industrial water | dye with treated water |
| --- | --- | --- |
| Degradation colour: | 4 | 4 |
| Staining on: |  |  |
| Wool | 4-5 | 4-5 |
| Acrylic | 4-5 | 4-5 |
| Polyester | 4-5 | 4-5 |
| Polyamide | 4-5 | 4-5 |
| Cotton | 4-5 | 4-5 |
| Acetate | 4-5 | 4-5 |

The differences in colour fastness expressed are not significant.

##### Colour fastness to rubbing

| DYEING IN INDUSTRIAL WATER |  | DYEING IN TREATED WATER |  |
| --- | --- | --- | --- |
| colour fastness to rubbing |  | colour fastness to rubbing |  |
| dry | wet | dry | wet |
| grey colour |  |  |  |
| 4-5 | 4-5 | 4-5 | 4-5 |
| blue sea colour |  |  |  |
| 4-5 | 4-5 | 4-5 | 4-5 |

As outlined there is no longer any variation between  colourfastness to rubbing  in the samples dyed in using two types of water.

##### Conclusions: reuse of permeate for scouring and disperse dyeing of polyester

In general the differences revealed at the end of each test is of little significance as they do not indicate any particular problem.

The results obtained with treated water, in reference to the materials used in the  laboratory can be considered equal to those obtained by using industrial water.

## Acid dyeing (Polyamide dyeing and silk dyed rinsing)

In the present chapter, discussion and results of the experimental activities carried out on the two acid dyeing effluents is reported. In the table below, the treatments carried out on each effluent is synthesized:

| Process Effluent | UF | NF | UF+NF | Anaer. + UF | Anaer. + NF | Anaer. +UF+NF |
| --- | --- | --- | --- | --- | --- | --- |
| Polyamide acid dyeing (PAD) | X |  | X | X | X | X |
| Silk acid dyeing rinsing (SADR) |  | X |  |  |  |  |

### Anaerobic tests results (Polyamide dyeing)

Results of the experiment are represented at three different wavelengths. It was not possible to choose such wavelengths that the three colour areas were represented due to the dominance of absorption in the blue area. Based on the spectrum the following wavelengths were chosen. One in the yellow area (475 nm), and two in the blue area (585 nm and 620 nm).

#### Results of batch experiments

In the following sections the results of the experiments with acid dyeing wastewater will be described. In total the mesophilic experiment lasted 17 days, but the thermophilic experiment with the same wastewater, carried out by Dos Santos (2003b), who took a much shorter experimental time, lasted only 5 days. Therefore, most graphs cover a time span of only a week, to be able to give a clear comparison of the two conditions. Figure 51 shows the mesophilic experiment, during the complete treatment time, for absorption at 620 nm (the main maximum absorption wavelength for the wastewater). The UV-VIS spectra of the reactive dyeing incubations at different time intervals can be found in Appendix C.

Figure 51 - Decolourisation of acid dyeing wastewater at 30C. ♦ = chemical control, ● = sludge + w.w., x = sludge + w.w. + AQS, Δ = sludge + w.w. + size, □ = sludge + w.w. + size + AQS, ▲ = sludge + w.w. + VFA-Glucose, ■ = sludge + w.w. + VFA-Glucose + AQS.

As can be seen in the graph, all incubations with sludge and cosubstrate (VFA/Glucose or size liquid) reach the same ultimate decolourisation level after 17 days. The combination of sludge and cosubstrate is clearly needed for a fast decolourisation, indicating that decolourisation is (at least partly) the result of biological activity. It is striking that the other three incubations show a significant decolourisation after some time. Apparently, chemical processes are also involved. This is confirmed by the formation of blue precipitates (in form of flocs) in many of the bottles, causing decolourisation of the liquid phase. In the biologically active incubations, there seems to be less blue precipitate present, but it is very difficult to quantify the precipitate. In the bottles incubated with sludge, cosubstrate and AQS the precipitate looks more grey than blue.

##### Mesophilic and thermophilic decolourisation with VFA-Glucose as cosubstrate

The results of the experiment are presented in Figure 52, in three different graphs. Each graph representing a different wavelength.

At the higher wavelengths the chemical control shows distinctively lower decolourisation rates. Colour removal is clearly a biological process, as the addition of co-substrate stimulates the decolourisation rates. In comparison to mesophilic conditions, thermophilic conditions speed up the process. At 475 nm the results are less clear. Strangely, the mesophilic chemical control is hardly different from the mesophilic bottles with sludge present. The thermophilic chemical control behaves more as expected, that is, negligible decolourisation.

##### The effect of AQS on meso- and thermophilic decolourisation with VFA-Glucose

During the thermophilic decolourisation of acid dyeing wastewater in presence of AQS no difference can be observed for batches with VFA-glucose at high wavelengths (see Figure 53). At 475 nm there is a difference, but not as expected. Instead of improving decolourisation, absorption values increase in time. This effect did not occur in AQS-free incubations. Mesophilic incubations do show an effect of AQS at higher wavelengths, but the effect is small. Similarly to the thermophilic result, at 475 nm an increase in absorption can be seen for the incubation with AQS.

##### Decolourisation with size as cosubstrate in presence and absence of AQS

This experiment was only done at 30C. In presence of size as a cosubstrate, AQS increases decolourisation rates more than for VFA-glucose as cosubstrate at higher wavelengths (Figure 54). Again, at 475 nm the AQS amended culture shows an increase in absorption values.

##### Comparison of co-substrates and AQS concentration

In Figure 55 two parameters are compared. The type of cosubstrate (size or VFA-glucose), and the effect of two different concentrations of AQS. Size in presence of 0.5 mM AQS performs best. However, VFA-glucose in presence of 0.05 mM AQS seems to speed up after 6 days, ending at almost the same final decolourisation. Between the other batches there is almost no difference. At 475 nm there was again an increase in absorption values that decreased after some time.

#### Control experiment for possible biological activity of size

Because of the strange results with size and AQS for the acid dyeing wastewater batch experiments, a control experiment needed to be conducted to check for biological activity of the size due to the quite long time it had been in storage. The amount of acid dyeing wastewater left was not sufficient to conduct this experiment, and therefore it was carried out with a different dark blue acid dyeing wastewater. This wastewater was still available from other experiments with textile wastewater carried out in the lab. It was a dark acid dyeing wastewater sample from Italy. The exact composition is unknown, but the shape of the UV/VIS spectrum of both waters is very similar. Size was sterilised by autoclaving for 20 minutes at 120C. This experiment revealed no significant difference between sterilised size, non-sterilised size, and VFA-Glucose as co-substrate. It can be concluded that the size is not biologically active, storage at 4C apparently was effective. For this Italian wastewater, no difference was observed between the results for size and VFA-glucose in presence and absence of a mediator.

| 475 nm |  | 475 nm |
| --- | --- | --- |
| 585 nm |  | 585 nm |
| 620 nm |  | 620 nm |
| Figure 52 – Decolourisation of acid dyeing wastewater in presence and absence of co-substrate at 30C (open symbols) and 55C (filled symbols). ◊ = chemical control, o = sludge + w.w., Δ = sludge + w.w. + VFA/glucose as cosubstrate. |  | Figure 53 – Decolourisation of acid dyeing wastewater in presence and absence of 0.5 mM AQS at 30C (open symbols) and 55C (filled symbols). ◊ = chemical control, o = sludge + w.w. + AQS, Δ = sludge + w.w. + VFA/glucose, □ = sludge + w.w. + VFA/glucose + AQS. |

| 475 nm |  | 475 nm |
| --- | --- | --- |
| 585 nm |  | 585 nm |
| 620 nm |  | 620 nm |
| Figure 54 – Decolourisation of acid dyeing wastewater with size, in presence and absence of 0.5 mM AQS at 30C. ◊ = chemical control, o = sludge + w.w., x = sludge + w.w. + AQS, Δ = sludge + w.w. + size, □ = sludge + w.w. + size + AQS. |  | Figure 55 – Decolourisation of acid dyeing wastewater with size (open symbols) or VFA-glucose (closed symbols), in presence and absence of 0.5 or 0.05 mM AQS at 30C. Δ = sludge + w.w. + cosubstrate, o = sludge + w.w. + cosubstrate + 0.05 mM AQS, □ = sludge + w.w. + cosubstrate + 0.5 mM AQS. |

#### Results of the continuous experiment

The goal of the continuous experiment of acid dyeing wastewater was to investigate the potential of anaerobic treatment as a pre-treatment step before membrane filtration (see Introduction). Figure 56 gives the results for decolourisation, methane production and COD-removal.

Figure 56 - Continuous experiment with acid dyeing wastewater in an EGSB-type reactor.  = 420 nm, ■ = 500 nm, ▲ = 620 nm, o = methane production, ● = COD removal.

The first vertical line indicates the change of wastewater to wastewater with size added as co-substrate, the second line the feeding of the collected effluent as influent after treating all the wastewater. As can be seen in Figure 56, adding a co-substrate to the wastewater increased the colour removal. Decolourisation was steadily increasing at the three wavelengths. COD removal and methane production however, were steadily decreasing. When the reactor is fed with its own effluent, colour removal keeps increasing (see also Figure 57).

Figure 57 - Visible colour of the acid dyeing influent and its two consecutive effluents. Left: reactive dyeing influent, middle: first effluent (sample day 20), right: effluent after re-treatment of the first effluent (sample day 30).

Especially for the two higher wavelengths colour removal is high. This is probably due to the formation of precipitates in the reactor effluent, just like the precipitates that were observed in the batch test. If flocs were formed, the granular sludge would behave like a filter and retain them in the reactor.

### Membrane treatment results

#### Direct NF results

Direct nanofiltration has been applied on SADR effluent. The results of the tests carried out according to the methods described above, on bench scale and on pilot scale are here reported.

##### Bench scale NF on SADR effluent

###### Characterization of SADR/NF

Flow rate measurements at 6 bar pressure for three membranes at varying temperature and reported at 25 °C:

| P 6 bar | Membrane | T [°C] | QT [ l ·h-1·m-2 ] | k | Q25 [ l ·h-1·m-2 ] |
| --- | --- | --- | --- | --- | --- |
|  | DK | 35 | 61 | 0.028 | 46 |
|  | DL | 33 | 92 | 0.023 | 77 |
|  | HL | 34 | 85 | 0.027 | 66 |

###### Complete recirculation test of SADR/NF

Flow rate decrease passing to real effluent filtration:

| P 6 bar | Membrane | Q25 [ l · h-1· m-2 ] | Flow rate decrease [%] |
| --- | --- | --- | --- |
|  | DK | 40 | 14 |
|  | DL | 59 | 24 |
|  | HL | 55 | 18 |

Permeates quality:

|  | Feed | DK | DL | HL |
| --- | --- | --- | --- | --- |
| pH | 7.4 | 7.5 | 7.6 | 7.4 |
| Conductivity [S·cm-1] | 1626 | 582 | 819 | 643 |
| Turbidity [NTU] | 2.9 | 0.22 | 0.31 | 0.17 |
| Abs  = 426 nm | 0.040 | 0.006 | 0.010 | 0.006 |
| Abs  = 558 nm | 0.055 | 0.004 | 0.009 | 0.004 |
| Abs  = 660 nm | 0.025 | 0.009 | 0.008 | 0.008 |
| TOC [mg · l-1] | 18 | 3 | 4 | 7 |
| TC [mg · l-1] | 28 | 5 | 7 | 9 |
| IC [mg · l-1] | 10 | 2 | 3 | 2 |

###### Choice of the membrane for the pilot scale

The decrease of flow rate passing from deionised water to real effluent filtration is high for all the three membranes. DK has the best fluid-dynamic affinity.

Membrane DK also have the best removal efficiency on salinity, colour in reference to DL and on organic carbon content in reference to HL.

DK is chosen for further investigation.

##### Pilot scale NF on SADR effluent

###### Pi. Sc. characterization of SADR/NF

Flow rates at different pressure values:

| p [ bar ] | Q30 [ l · h-1] | Q33 [ l · h-1] | Q35 [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- | --- |
| 6 | 15 | 16 | 17 | 12 |
| 6.9 | 18 | 18 | 20 | 13 |
| 9 | 24 | 25 | 26 | 18 |

###### Pi. Sc. complete recirculation test of SADR/NF

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 30 | 13 | 11 |
| 15 | 32 | 14 | 11 |
| 30 | 33 | 14 | 11 |
| 45 | 34 | 14 | 11 |
| 60 | 35 | 15 | 11 |

|  | Feed | permeate 0' | permeate 60' |
| --- | --- | --- | --- |
| pH | 7.5 | 7.3 | 7.5 |
| Conductivity [S·cm-1] | 1619 | 488 | 451 |
| Turbidity [NTU] | 4.0 | 0.3 | 0.4 |
| Abs  = 426 nm | 0.040 | 0.011 | 0.009 |
| Abs  = 558 nm | 0.055 | 0.011 | 0.004 |
| Abs  = 660 nm | 0.025 | 0.007 | 0.003 |
| TOC [mg · l-1] | 33 | 19 | 26 |
| TC [mg · l-1] | 41 | 21 | 29 |
| IC [mg · l-1] | 8 | 2 | 2 |

###### Concentration effect test of SADR/NF

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 35 | 15 | 11 |
| 20 | 36 | 15 | 11 |
| 40 | 37 | 15 | 11 |
| 60 | 38 | 15 | 10 |
| 80 | 39 | 14 | 9 |

|  | Feed | perm. 0% | perm. 20% | perm. 40% | perm. 60% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 7.5 | 7.3 | 7.4 | 8.1 | 9.0 | 8.4 | 7.4 |
| Conductivity [S·cm-1] | 1619 | 478 | 565 | 735 | 1019 | 1692 | 4570 |
| Turbidity [NTU] | 4.0 | 0.4 | 0.5 | 0.4 | 0.4 | 0.4 | 15.4 |
| SST [mg · l-1] | 5.5 | - | - | - | - | - | 30 |
| Abs  = 426 nm | 0.040 | 0.003 | 0.006 | 0.007 | 0.006 | 0.013 | 0.090 |
| Abs  = 558 nm | 0.055 | 0.004 | 0.003 | 0.003 | 0.003 | 0.007 | 0.095 |
| Abs  = 660 nm | 0.025 | 0.003 | 0.003 | 0.002 | 0.003 | 0.004 | 0.031 |
| TOC [mg · l-1] | 33 | 26 | 23 | 18 | 18 | 24 | 65 |
| TC [mg · l-1] | 41 | 29 | 25 | 22 | 24 | 32 | 91 |
| IC [mg · l-1] | 8 | 2 | 2 | 3 | 5 | 8 | 26 |

♦ TOC in the feed

■ TOC in the permeate

###### Second characterization of SADR/NF

Flow rates in the second characterization and comparison between first and second characterization:

| p [ bar ] | Q30 [ l · h-1] | Q33 [ l · h-1] | Q35 [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- | --- |
| 6 | 15 | 16 | 17 | 12 |
| 6.9 | 18 | 18 | 20 | 13 |
| 9 | 24 | 25 | 26 | 18 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 6 | 12 | 12 | 0 |
| 6.9 | 13 | 13 | 0 |
| 9 | 17 | 18 | -5 |

###### Conclusions of SADR/NF

During the nanofiltration with real effluent on pilot scale, a slight decrease in the flow rate is observable, showing a quite good affinity.

The concentration effect test showed that the flow rate stays almost constant at varying feed concentration, a sensible decrease is observable over the 60% of increase in concentration (volume reduction).

The second characterization is performed without any loss in the flow rate with reference to the first one.

The quality of the permeate is acceptable for reuse tests even if some abatement percentile are low (organic content, colour, conductivity –due to the presence of mono-valent salts) due to the good quality of the feed.

Comparison among flow rates measured in all the pilot scale trials:

Quality of the aver. permeate and percentage abatement

|  | Feed | Permeate | Abatement % |
| --- | --- | --- | --- |
| pH | 7.5 | 8.0 | - |
| Conductivity [S·cm-1] | 1619 | 898 | 45 |
| Turbidity [NTU] | 4.0 | 0.4 | 90 |
| SST [NTU] | 5.5 | - | >99 |
| Abs  = 426 nm | 0.040 | 0.010 | 75 |
| Abs  = 558 nm | 0.055 | 0.008 | 85 |
| Abs  = 660 nm | 0.025 | 0.006 | 76 |
| TOC [mg · l-1] | 33 | 22 | 34 |
| TC [mg · l-1] | 41 | 26 | 36 |
| IC [mg · l-1] | 8 | 2 | 2 |

#### UF results

UF membrane choice was performed on the base of previous experimental results. Membrane labelled MW, produced by Osmonics Inc. was selected. Investigation was carried out on pilot scale.

##### Pilot scale UF on PAD effluent

###### Pi. Sc. characterization of PAD/UF

Flow rates at different pressure and temperature values:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 1.4 | 39 |
| 1.9 | 48 |
| 2.3 | 54 |
| 2.8 | 63 |

###### Pi. Sc. complete recirculation test of PAD/UF

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 20 | 42 | 44 |
| 20 | 20 | 42 | 44 |
| 40 | 21 | 43 | 44 |
| 60 | 21 | 43 | 44 |

|  | Feed | permeate 0' | permeate 60' |
| --- | --- | --- | --- |
| pH | 7.4 | 7.2 | 7.6 |
| Conductivity [S·cm-1] | 830 | 749 | 748 |
| Abs  = 426 nm | 1.402 | 0.027 | 0.023 |
| Abs  = 558 nm | 1.693 | 0.013 | 0.010 |
| Abs  = 660 nm | 1.567 | 0.012 | 0.005 |
| Abs  = 436 nm | 1.316 | 0.027 | 0.023 |
| Abs  = 525 nm | 1.384 | 0.015 | 0.012 |
| Abs  = 620 nm | 1.912 | 0.013 | 0.008 |
| TOC [mg · l-1] | 480 | 226 | 227 |
| TC [mg · l-1] | 490 | 235 | 237 |
| IC [mg · l-1] | 10 | 9 | 10 |
| SST [mg l –1] | 10 | - | - |

###### Concentration effect test of PAD/UF

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 21 | 43 | 44 |
| 40 | 22 | 42 | 43 |
| 80 | 22 | 40 | 41 |

|  | Feed | perm. 0% | perm. 40% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- |
| pH | 7.4 | 7.6 | 7.6 | 7.5 | 7.4 |
| Conductivity [S·cm-1] | 830 | 748 | 780 | 835 | 920 |
| TOC [mg · l-1] | 480 | 227 | 235 | 249 | 1278 |
| TC [mg · l-1] | 490 | 237 | 245 | 259 | 1292 |
| IC [mg · l-1] | 10 | 10 | 10 | 10 | 14 |
| Abs  = 426 nm | 1.402 | 0.023 | 0.025 | 0.035 | 4.222 |
| Abs  = 558 nm | 1.693 | 0.01 | 0.011 | 0.012 | 4.387 |
| Abs  = 660 nm | 1.567 | 0.005 | 0.006 | 0.009 | 2.637 |
| Abs  = 436 nm | 1.316 | 0.023 | 0.026 | 0.035 | 4.208 |
| Abs  = 525 nm | 1.384 | 0.012 | 0.014 | 0.017 | 4.319 |
| Abs  = 620 nm | 1.912 | 0.008 | 0.009 | 0.012 | 2.617 |
| SST [mg · l-1] | 10.5 | - | - | - | 37.3 |

###### Second characterization of PAD/UF

Flow rates in the second characterization and comparison between first and second characterization:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 1.4 | 39 |
| 1.9 | 47 |
| 2.3 | 54 |
| 2.8 | 63 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 2.1 | 51 | 51 | - |

###### Conclusions of PAD/UF

The effluent affinity for the membrane is quite good.

Little loss of flow rate is observable during the concentration effect test.

Very good recovery of the initial maximum flow rate was observed.

The quality of the permeate is not good enough for reuse purpose because of too high value of the remaining organic content and colour above the visible threshold in spite of quite good removals.

Comparison among flow rates measured in all the pilot scale trials:

Comparison among flow rates measured in all the pilot scale trials:

|  | Feed | Permeate UF | Abatement |
| --- | --- | --- | --- |
| pH | 7.4 | 7.6 |  |
| Conductivity [S·cm-1] | 830 | 788 | 5% |
| TOC [mg · l-1] | 480 | 237 | 51% |
| TC [mg · l-1] | 490 | 247 | 50% |
| IC [mg · l-1] | 10 | 10 | 0% |
| Abs  = 426 nm | 1.402 | 0.028 | 98% |
| Abs  = 558 nm | 1.693 | 0.011 | 99% |
| Abs  = 460 nm | 1.567 | 0.007 | >99% |
| Abs  = 436 nm | 1.316 | 0.028 | 98% |
| Abs  = 525 nm | 1.384 | 0.014 | 99% |
| Abs  = 620 nm | 1.912 | 0.010 | 99% |
| SST [m l-1] | 10.5 | - | >99% |

The permeate effluent from ultrafiltration is submitted to nanofiltration as described in § 4.6.2.3.1.

#### UF +NF results

##### Pilot scale NF on PAD effluent after UF

###### Pi. Sc. characterization of PAD/NF

Flow rates at different pressure values:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 6 | 20 |
| 6.9 | 23 |
| 9 | 29 |

###### Pi. Sc. complete recirculation test of PAD/NF

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 22 | 19 | 20 |
| 20 | 25 | 21 | 21 |
| 40 | 26 | 21 | 21 |
| 60 | 26 | 22 | 22 |

|  | Feed | permeate 0' | permeate 60' |
| --- | --- | --- | --- |
| pH | 7.5 | 7.5 | 7.5 |
| Conductivity [S·cm-1] | 788 | 192 | 191 |
| Abs  = 426 nm | 0.018 | 0.001 | 0.003 |
| Abs  = 558 nm | 0.008 | 0.000 | 0.005 |
| Abs  = 660 nm | 0.011 | 0.005 | 0.007 |
| Abs  = 436 nm | 0.028 | 0.002 | 0.003 |
| Abs  = 525 nm | 0.012 | 0.000 | 0.002 |
| Abs  = 620 nm | 0.009 | 0.002 | 0.007 |
| TOC [mg · l-1] | 256 | 40 | 46 |
| TC [mg · l-1] | 266 | 47 | 53 |
| IC [mg · l-1] | 10 | 7 | 7 |
| SST [g l -1] | - | - | - |

###### Concentration effect test of PAD/NF (membrane DK)

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 26 | 22 | 22 |
| 30 | 26 | 22 | 22 |
| 60 | 28 | 21 | 20 |

|  | Feed | perm. 0% | perm. 30% | perm. 60% | Conc. |
| --- | --- | --- | --- | --- | --- |
| pH | 7 | 8 | 7 | 7 | 8 |
| Conductivity [S·cm-1] | 788 | 191 | 238 | 322 | 1403 |
| TOC [mg · l-1] | 256 | 53 | 66 | 66 | 434 |
| TC [mg · l-1] | 265 | 60 | 73 | 74 | 446 |
| IC [mg · l-1] | 10 | 7 | 8 | 8 | 12 |
| Abs  = 426 nm | 0 | 0 | 0 | 0 | 0 |
| Abs  = 558 nm | 0.010 | 0.005 | 0.001 | 0.001 | 0.021 |
| Abs  = 660 nm | 0.006 | 0.007 | 0.001 | 0.002 | 0.013 |
| Abs  = 436 nm | 0.025 | 0.003 | 0.001 | 0.002 | 0.055 |
| Abs  = 525 nm | 0.012 | 0.002 | 0.001 | 0.001 | 0.022 |
| Abs  = 620 nm | 0.009 | 0.007 | 0.001 | 0.002 | 0.020 |
| SST [mg · l-1] | 0.77 | - | - | - | 3.85 |

###### Second characterization of PAD/NF

Flow rates in the second characterization and comparison among first, second and after washing characterization:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 6 | 19 |
| 6.9 | 23 |
| 9 | 30 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 6.9 | 23 | 23 | - |

###### Conclusions of PAD/NF

The affinity shown by the effluent PAD for the membrane is good.

Low decrease is also observable at increasing concentrations. A complete recovery of the maximum flow rate is obtained during the second characterization.

The quality of the permeate is very good due to the high removals performed.

Comparison among flow rates measured in all the pilot scale trials:

Quality of the aver. permeate and percentage abatement:

|  | Feed | Permeate NF | Abatement % |
| --- | --- | --- | --- |
| pH | 7 | 7 |  |
| Conductivity [S·cm-1] | 788 | 250 | 68% |
| TOC [mg · l-1] | 256 | 62 | 76% |
| TC [mg · l-1] | 265 | 69 | 74% |
| IC [mg · l-1] | 10 | 8 | 22% |
| Abs  = 426 nm | 0.024 | 0.002 | 90% |
| Abs  = 558 nm | 0.010 | 0.002 | 78% |
| Abs  = 460 nm | 0.006 | 0.003 | 40% |
| Abs  = 436 nm | 0.025 | 0.002 | 91% |
| Abs  = 525 nm | 0.012 | 0.002 | 87% |
| Abs  = 620 nm | 0.009 | 0.003 | 63% |

Overall removal efficiency of the train UF + NF, obtained combining the results of the single treatments:

|  | Abatement % UF | Abatement % NF | Overall Efficiency % |
| --- | --- | --- | --- |
| pH | - | - | - |
| Conductivity [S·cm-1] | 5% | 68% | 70% |
| TOC [mg · l-1] | 51% | 76% | 88% |
| TC [mg · l-1] | 50% | 74% | 87% |
| IC [mg · l-1] | 0% | 22% | 22% |
| Abs  = 426 nm | 98% | 90% | >99% |
| Abs  = 558 nm | 99% | 78% | >99% |
| Abs  = 460 nm | >99% | 40% | >99% |
| Abs  = 436 nm | 98% | 91% | >99% |
| Abs  = 525 nm | 99% | 87% | >99% |
| Abs  = 620 nm | 99% | 63% | >99% |
| SST (mg l-1) | >99%! | - | >99% |

#### Anaerobically pretreated PAD -direct NF results

The membrane choice was not performed on bench scale test results. The membrane DL has been chosen on the base of previous results on similar effluents.

##### Pilot scale NF on PAD effluent anaerobically pretreated

###### Pi. Sc. characterization of PAD/NF after anaer. treatm.

Flow rates at different pressure values:

| p [ bar ] | Q33 [ l · h-1] | Q35 [ l · h-1] | Q38 [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- | --- |
| 6 | 23 | 25 | 26 | 20 |
| 6.9 | 27 | 29 | 30 | 23 |
| 9 | 36 | 36 | 38 | 30 |

###### Pi. Sc. complete recirculation test of PAD/NF after anaer. treatm.

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 32 | 21 | 20 |
| 15 | 37 | 23 | 20 |
| 30 | 38 | 24 | 20 |
| 45 | 39 | 24 | 20 |
| 60 | 39 | 24 | 20 |

|  | Feed | permeate 0' | permeate 60' |
| --- | --- | --- | --- |
| pH | 8.8 | 8.6 | 9.1 |
| Conductivity [S·cm-1] | 1438 | 656 | 652 |
| Abs  = 426 nm | 0.528 | 0.015 | 0.012 |
| Abs  = 558 nm | 0.247 | 0.002 | 0.003 |
| Abs  = 660 nm | 0.117 | 0.001 | 0.002 |
| Abs  = 436 nm | 0.525 | 0.015 | 0.013 |
| Abs  = 525 nm | 0.331 | 0.006 | 0.005 |
| Abs  = 620 nm | 0.163 | 0.000 | 0.003 |
| TOC [mg · l-1] | 161 | 7 | 8 |
| TC [mg · l-1] | 286 | 73 | 108 |
| IC [mg · l-1] | 125 | 66 | 100 |

###### Concentration effect test of PAD/NF after anaer. treatm.

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 41 | 27 | 20 |
| 30 | 41 | 27 | 20 |
| 60 | 41 | 26 | 20 |

|  | Feed | perm. 0% | perm. 30% | perm. 60% | Conc. |
| --- | --- | --- | --- | --- | --- |
| pH | 8.8 | 9.1 | 9.1 | 9.0 | 8.7 |
| Conductivity [S·cm-1] | 1438 | 652 | 749 | 950 | 2160 |
| Abs  = 426 nm | 0.528 | 0.012 | 0.018 | 0.018 | 1.147 |
| Abs  = 558 nm | 0.247 | 0.003 | 0.004 | 0 | 0.55 |
| Abs  = 660 nm | 0.117 | 0.002 | 0.002 | 0.002 | 0.266 |
| Abs  = 436 nm | 0.525 | 0.013 | 0.019 | 0.021 | 1.139 |
| Abs  = 525 nm | 0.331 | 0.005 | 0.008 | 0.007 | 0.728 |
| Abs  = 620 nm | 0.163 | 0.003 | 0 | 0 | 0.366 |
| TOC [mg · l-1] | 161 | 8 | 20 | 9 | 311 |
| TC [mg · l-1] | 286 | 108 | 82 | 72 | 543 |
| IC [mg · l-1] | 125 | 100 | 62 | 63 | 232 |
| SST [mg · l-1] | 8.0 | - | - | - | 14.7 |

###### Second characterization of PAD/NF after anaer. treatm.

Flow rates in the second characterization and comparison between first and second characterization:

| p [ bar ] | Q33 [ l · h-1] | Q35 [ l · h-1] | Q38 [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- | --- |
| 6 | 21 | 22 | 26 | 19 |
| 6.9 | 25 | 26 | 29 | 22 |
| 9 | 33 | 34 | 38 | 28 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 6 | 20 | 19 | 5 |
| 6.9 | 23 | 22 | 4 |
| 9 | 30 | 28 | 7 |

###### Conclusions of PAD/NF after anaer. treatm.

From the fluydodynamic point of view, the behaviour is good in terms of affinity, concentration effect and recovery in the second characterization,

The quality of the permeate is good due to the high removals but the colour is still over the visible threshold.

Comparison among flow rates measured in all the pilot scale trials.

Quality of the aver. permeate and percentage abatement

|  | Feed | Permeate | Abatement % |
| --- | --- | --- | --- |
| pH | 8.8 | 9.1 | - |
| Conductivity [S·cm-1] | 1438 | 783.7 | 46% |
| Abs  = 426 nm | 0.528 | 0.016 | 97% |
| Abs  = 558 nm | 0.247 | 0.002 | 99% |
| Abs  = 660 nm | 0.117 | 0.002 | 98% |
| Abs  = 436 nm | 0.525 | 0.018 | 97% |
| Abs  = 525 nm | 0.331 | 0.007 | 98% |
| Abs  = 620 nm | 0.163 | 0.001 | 99% |
| TOC [mg · l-1] | 161 | 12.3 | 92% |
| TC [mg · l-1] | 286 | 87.3 | 69% |
| IC [mg · l-1] | 125 | 75.0 | 40% |
| SST [mg · l-1] | 8.0 | - | >99 |

#### Anaerobically pretreated PAD -UF results

UF membrane choice was performed on the base of previous experimental results. Membrane labelled MW, produced by Osmonics Inc. was selected. Investigation was carried out on pilot scale.

##### Pilot scale UF on PAD effluent anaerobically pretreated

###### Pi. Sc. characterization of PAD/UF anaerobically pretreated

Flow rates at different pressure and temperature values:

| p [ bar ] | Q28 [ l · h-1] | Q30 [ l · h-1] | Q33 [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- | --- |
| 1.4 | 38 | 39 | 40 | 38 |
| 1.9 | 46 | 49 | 49 | 46 |
| 2.3 | 52 | 55 | 55 | 51 |
| 2.8 | 60 | 63 | 63 | 60 |

###### Pi. Sc. complete recirculation test of PAD/UF anaerobically pretreated

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 23 | 39 | 40 |
| 15 | 24 | 33 | 33 |
| 30 | 24 | 32 | 32 |
| 45 | 25 | 31 | 31 |
| 60 | 25 | 30 | 30 |

|  | Feed | permeate 0' | permeate 60' |
| --- | --- | --- | --- |
| pH | 7.6 | 7.9 | 8.1 |
| Conductivity [S·cm-1] | 1450 | 1402 | 1378 |
| Abs  = 426 nm | 0.455 | 0.196 | 0.145 |
| Abs  = 558 nm | 0.212 | 0.069 | 0.043 |
| Abs  = 660 nm | 0.099 | 0.026 | 0.012 |
| Abs  = 436 nm | 0.458 | 0.209 | 0.159 |
| Abs  = 525 nm | 0.290 | 0.118 | 0.087 |
| Abs  = 620 nm | 0.142 | 0.037 | 0.018 |
| TOC [mg · l-1] | 98 | 39 | 27 |
| TC [mg · l-1] | 251 | 186 | 175 |
| IC [mg · l-1] | 153 | 147 | 148 |

###### Concentration effect test of PAD/UF anaerobically pretreated

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 25 | 30 | 30 |
| 40 | 25 | 31 | 31 |
| 80 | 25 | 31 | 31 |

|  | Feed | perm. 0% | perm. 40% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- |
| pH | 7.6 | 8.1 | 8.3 | 8.2 | 7.3 |
| Conductivity [S·cm-1] | 1450 | 1378 | 1411 | 1444 | 1570 |
| Abs  = 426 nm | 0.455 | 0.145 | 0.078 | 0.223 | 1.016 |
| Abs  = 558 nm | 0.212 | 0.043 | 0.06 | 0.079 | 0.535 |
| Abs  = 660 nm | 0.099 | 0.012 | 0.019 | 0.029 | 0.269 |
| Abs  = 436 nm | 0.458 | 0.159 | 0.193 | 0.236 | 0.996 |
| Abs  = 525 nm | 0.29 | 0.087 | 0.11 | 0.136 | 0.668 |
| Abs  = 620 nm | 0.142 | 0.018 | 0.028 | 0.04 | 0.387 |
| TOC [mg · l-1] | 98 | 27 | 39 | 40 | 238 |
| TC [mg · l-1] | 251 | 175 | 186 | 193 | 406 |
| IC [mg · l-1] | 153 | 148 | 147 | 153 | 168 |
| SST [mg · l-1] | 16.7 | - | - | - | 44.2 |

###### Second characterization of PAD/UF anaerobically pretreated

Flow rates in the second characterization and comparison between first and second characterization:

| p [ bar ] | Q28 [ l · h-1] | Q30 [ l · h-1] | Q33 [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- | --- |
| 1.4 | 38 | 38 | 39 | 37 |
| 1.9 | 45 | 48 | 48 | 45 |
| 2.3 | 50 | 52 | 52 | 49 |
| 2.8 | 59 | 61 | 61 | 58 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 1.4 | 38 | 37 | 3 |
| 1.9 | 46 | 45 | 2 |
| 2.3 | 51 | 49 | 4 |
| 2.8 | 60 | 58 | 3 |

###### Conclusions of PAD/UF anaerobically pretreated

The loss in flow rate passing from pure water to the real pre-treated effluent is evident (the affinity membrane/effluent was better with the not pre-treated effluent).

The flow rate recovery during the second characterization is good.

The quality of the permeate is not good enough for reuse purposes due to colour removals sensibly lower than those encountered with UF treatment of raw effluent.

Comparison among flow rates measured in all the pilot scale trials.

Comparison among flow rates measured in all the pilot scale trials

|  | Feed | Permeate UF | Abatement % |
| --- | --- | --- | --- |
| pH | 7.6 | 8.2 |  |
| Conductivity [S·cm-1] | 1450 | 1411.0 | 3% |
| TOC [mg · l-1] | 98 | 35.3 | 64% |
| TC [mg · l-1] | 251 | 184.7 | 26% |
| IC [mg · l-1] | 153 | 149.3 | 2% |
| Abs  = 426 nm | 0.455 | 0.149 | 67% |
| Abs  = 558 nm | 0.212 | 0.061 | 71% |
| Abs  = 460 nm | 0.099 | 0.020 | 80% |
| Abs  = 436 nm | 0.458 | 0.196 | 57% |
| Abs  = 525 nm | 0.290 | 0.111 | 62% |
| Abs  = 620 nm | 0.142 | 0.029 | 80% |
| SST [m l-1] | 16.7 | - | >99 |

The permeate effluent from ultrafiltration is submitted to nanofiltration as described in § 4.6.2.6.1.

#### Anaerobically pretreated PAD -UF+NF results

Membrane DL was used for pilot scale tests without the bench scale test selection.

##### Pilot scale NF on anaerobically pretreated PAD effluent after UF

###### Pi. Sc. characterization of anaerobically pretreated PAD/NF after UF

Flow rates at different pressure values:

| p [ bar ] | Q33 [ l · h-1] | Q35 [ l · h-1] | Q38 [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- | --- |
| 6 | 24 | 26 | 27 | 21 |
| 6.9 | 28 | 29 | 31 | 24 |
| 9 | 36 | 36 | 40 | 30 |

###### Pi. Sc. complete recirculation test of anaerobically pretreated PAD/NF after UF

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 33 | 24 | 20 |
| 15 | 36 | 27 | 22 |
| 30 | 37 | 27 | 21 |
| 45 | 38 | 27 | 21 |
| 60 | 38 | 27 | 21 |

|  | Feed | permeate 0' | permeate 60' |
| --- | --- | --- | --- |
| pH | 8.8 | 8.7 | 9.1 |
| Conductivity [S·cm-1] | 1407 | 653 | 650 |
| Abs  = 426 nm | 0.212 | 0.014 | 0.019 |
| Abs  = 558 nm | 0.063 | 0.001 | 0.007 |
| Abs  = 660 nm | 0.023 | 0.000 | 0.002 |
| Abs  = 436 nm | 0.221 | 0.014 | 0.017 |
| Abs  = 525 nm | 0.112 | 0.005 | 0.009 |
| Abs  = 620 nm | 0.029 | 0.000 | 0.003 |
| TOC [mg · l-1] | 69 | 5 | 4 |
| TC [mg · l-1] | 184 | 61 | 59 |
| IC [mg · l-1] | 115 | 56 | 55 |

###### Concentration effect test of anaerobically pretreated PAD/NF after UF

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 38 | 27 | 21 |
| 30 | 38 | 27 | 21 |
| 60 | 38 | 24 | 19 |

|  | Feed | perm. 0% | perm. 30% | perm. 60% | Conc. |
| --- | --- | --- | --- | --- | --- |
| pH | 8.8 | 9.1 | 9.1 | 9.0 | 8.8 |
| Conductivity [S·cm-1] | 1407 | 650 | 736 | 902 | 2002 |
| TOC [mg · l-1] | 69 | 4 | 8 | 6 | 98 |
| TC [mg · l-1] | 185 | 58 | 67 | 85 | 308 |
| IC [mg · l-1] | 115 | 55 | 58 | 79 | 211 |
| Abs  = 426 nm | 0.207 | 0.017 | 0.023 | 0.019 | 0.385 |
| Abs  = 558 nm | 0.062 | 0.006 | 0.008 | 0.002 | 0.114 |
| Abs  = 660 nm | 0.020 | 0.002 | 0.007 | 0.001 | 0.032 |
| Abs  = 436 nm | 0.218 | 0.018 | 0.023 | 0.021 | 0.410 |
| Abs  = 525 nm | 0.112 | 0.010 | 0.011 | 0.008 | 0.212 |
| Abs  = 620 nm | 0.030 | 0.004 | 0.008 | 0.000 | 0.050 |

###### Second characterization of anaerobically pretreated PAD/NF after UF

Flow rates in the second characterization and comparison among first, second and after washing characterization:

| p [ bar ] | Q33 [ l · h-1] | Q35 [ l · h-1] | Q38 [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- | --- |
| 6 | 23 | 25 | 26 | 20 |
| 6.9 | 27 | 29 | 30 | 23 |
| 9 | 36 | 36 | 40 | 30 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 6.9 | 24 | 23 | 4 |

###### Conclusions of anaerobically pretreated PAD/NF after UF

From the fluydodynamic point of view, the behaviour is good in terms of affinity, concentration effect and recovery in the second characterization,

The quality of the permeate is not superior to the one obtained with direct filtration of the pre-treated effluent.

Comparison among flow rates measured in all the pilot scale trials.

Quality of the aver. permeate and percentage abatement

|  | Feed | Permeate NF | Abatement % |
| --- | --- | --- | --- |
| pH | 8.8 | 9.1 | - |
| Conductivity [S·cm-1] | 1407 | 762.7 | 46% |
| TOC [mg · l-1] | 69 | 6.0 | 91% |
| TC [mg · l-1] | 185 | 6.0 | 91% |
| IC [mg · l-1] | 115 | 63.9 | 45% |
| Abs  = 426 nm | 0.207 | 0.019 | 91% |
| Abs  = 558 nm | 0.062 | 0.006 | 91% |
| Abs  = 460 nm | 0.020 | 0.004 | 82% |
| Abs  = 436 nm | 0.218 | 0.021 | 91% |
| Abs  = 525 nm | 0.112 | 0.010 | 91% |
| Abs  = 620 nm | 0.030 | 0.004 | 87% |

Overall removal efficiency of the train UF + NF, obtained combining the results of the single treatments:

|  | Abatement % UF | Abatement % NF | Overall Efficiency % |
| --- | --- | --- | --- |
| pH | - | - | - |
| Conductivity [S·cm-1] | 3% | 46% | 47% |
| TOC [mg · l-1] | 64% | 91% | 97% |
| TC [mg · l-1] | 26% | 91% | 97% |
| IC [mg · l-1] | 2% | 45% | 46% |
| Abs  = 426 nm | 67% | 91% | 97% |
| Abs  = 558 nm | 71% | 91% | 97% |
| Abs  = 460 nm | 80% | 82% | 96% |
| Abs  = 436 nm | 57% | 91% | 96% |
| Abs  = 525 nm | 62% | 91% | 97% |
| Abs  = 620 nm | 80% | 87% | 97% |
| SST (mg l-1) | >99%! | - | >99% |

### Assessment of changes in aerobic biodegradability using respirometry

Textile dyes are often not aerobically degradable. This causes problems when treating dyeing water or mixed textile wastewater containing dyeing streams in a conventional activated sludge plant. Even in a factory where as much water as possible is reused, there will always be a rest-stream of wastewater that has to be treated before discharge. An activated sludge plant will often be involved, as an on-site end of pipe treatment or because the wastewater is discharged in a sewer and arrives in the municipal treatment plant. Anaerobic pre-treatment, attacking the dye molecules, can improve the aerobic biodegradability. Dye molecules are split in parts or the structures are changed. Respirometry can be used to determine the aerobic biodegradability of wastewater in activated sludge, and is in this case used to assess the aerobic biodegradability of the wastewater, the anaerobically treated sample and the membrane concentrates and permeate. Figure 58 shows the results. For clarity of the figure, only the trendlines have been made visible.

Figure 58 - Changes in aerobic biodegradability measured using respirometry. Tested amount was 50 ml for all samples.

The original wastewater gives no response, indicating that the acid dyeing wastewater is not aerobically biodegradable. Anaerobic treatment improves the biodegradability, and as can be seen in the response for the membrane concentrates, the biodegradable components are concentrated. The nanofiltration permeate however, gives only a small response, as expected.

### Tech./econ. feasibility of anaerobic treatment

Although the reactor set-up used in the experiments was not optimised, it can serve as a base for the full-size reactor calculation. The experimental reactor configuration for acid dyeing wastewater has been given in Table 9. Using this same configuration with the amount of wastewater as is available in the factory a full-scale reactor was calculated. Data on the discharged amounts of wastewater were taken from the PIDACS document of the respective company. See Table 18 for the results.

Table 18, Scale up to full size of the experimental reactor treating Polyamide (PA) acid dyeing wastewater. Two volumes were considered: the total wastewater volume coming from the same type of process as the wastewater tested in the reactor (discontinuous polyamide dyeing) and the wastewater volume of all dyeing processes performed in the factory.

|  |  |  | Discontinuous PA dyeing wastewater | All dyeing wastewater |
| --- | --- | --- | --- | --- |
| Reactor design | yearly supply of ww (Q) | m3/year | 59610 | 168274 |
|  | hourly supply of ww (Q) | m3/hour | 7 | 19 |
|  | Hydraulic residence time (HRT) | h | 16.2 | 16.2 |
|  | Chosen reactor height (H) | H | 5 | 5 |
|  | Reactor volume (Vr) | = Q * HRT | 110.2 | 311.2 |
|  | Reactor area (A) | = Vr / H | 22.0 | 62.2 |
|  | Upflow velocity (v) | = Q / A | 0.3 | 0.3 |
| Construction costs | Low estimation of construction costs in € | = 350 * m3 | € 38583 | € 108917 |
|  | High estimation of construction costs in € | = 500 * m3 | € 55119 | € 155596 |
| Cost calculation for high price / m3 reactor volume, based on 10 years of duration | Interest - average per year (1) | 4% / year | € 2662 | € 7771 |
|  | Maintenance (2) | 3% / year | € 1654 | € 4668 |
|  | Operation - manpower 0.25 person (3) | 12*1000 | € 12000 | € 12000 |
|  | Construction costs per year (4) | Costs/10 | € 5512 | 15560 |
|  | Total cost per year | sum 1 to 4 | € 21828 | € 39999 |
|  | Total costs per m3 wastewater |  | € 0.37 | € 0.24 |

To calculate the operational costs, it was assumed that manpower would consist of one person on a 25% job. Employing an operator costs a company around € 4000,- per month, so the total amount for one year of operation would be 12 x € 1000,-.

### Tech./econ. feasibility of membrane treatment

In the following paragraph the technical – economical aspects related to the treatment and reuse of the effluents are presented, independently from the considerations on permeates reusability exposed in the previous paragraphs.

In the table below, for all the treatments tested on acid dyeing effluents, the values of three flow indexes are reported as resulted from the experimental runs. I1 describes the affinity membrane – effluent, I2 the reduction of permeate flow at increased feed concentration and I3 is an estimation of the hours of operation before washing is required.

Refer to § 3.2.3.4. to have a description of how the indexes are calculated and their influence on the economical evaluations.

In the following tables and graphs all the details of the economical evaluations are reported for each effluent and treatment tested, in § 3.2.3.4. the method applied is explained with the assumptions behind it.

It can be noted that:

- The treatment trains tested UF, NF and UF+NF have shown a potentially high feasibility in terms of costs.

- The direct NF of anaerobically pretreated polyamide dyeing (PADa)effluent seems to be economically feasible. No advantages resulted in UF+NF treatment of anaerobically pretreated effluent.

#### Cost estimation UF/PAD

#### Cost estimation UF+NF/PAD

#### Cost estimation NF/SADR

#### Cost estimation UF/PADa

#### Cost estimation UF+NF/PADa

#### Cost estimation NF/PADa

### Reuse tests results (dyeing rinsing and printing)

#### Reuse of acid dyeing effluent (polyamide)

The permeate of acid dyeing has been reused for acid dyeing of polyamide both in a light and a dark colour shade.

##### Colour differences

|  | % permeate | delta E (CMC2:1) |
| --- | --- | --- |
| reference | 0% |  |
| light | 100% | 0,78 |
| light | 75% | 0,72 |
| reference | 0% |  |
| dark | 100% | 0,13 |
| dark | 75% | 0,22 |

For each colour shade the fabric, dyed with 100% fresh process water, has been taken as the reference to calculate the difference in colour. All values of delta E (colour difference) are below 0.8, which means that no significant changes in colour shade can be measured. Also visually no differences were observed.

##### Colour fastness to washing

|  | light |  |  | dark |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| %permeate | 0% | 100% | 75% | 0% | 100% | 75% |
| change of shade | 4-5 | 4 | 4-5 | 3-4 | 3 | 3 |
| staining |  |  |  |  |  |  |
| polyester | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 |
| cotton | 4-5 | 4-5 | 4-5 | 3-4 | 3-4 | 3 |

The differences between the reference and the treatments with reused permeate are always lower than 0.5.

##### Colour fastness to rubbing

|  | light |  |  | dark |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| % permeate | 0% | 100% | 75% | 0% | 100% | 75% |
| change of shade |  |  |  |  |  |  |
| dry | 5 | 5 | 5 | 5 | 5 | 5 |
| wet | 4-5 | 4-5 | 4-5 | 4 | 4 | 4 |
| staining |  |  |  |  |  |  |
| dry | 5 | 5 | 5 | 5 | 5 | 5 |
| wet | 5 | 5 | 5 | 5 | 5 | 5 |

All values are good to very good and no differences higher than 0.5 unit are noticed.

##### Conclusions: reuse of permeate for acid dyeing of polyamide

The waterquality of the acid dyeing permeate is good enough to be reused for acid dyeing of polyamide. No adaptations to the water quality are needed.

In the performed series of tests the reuse cycle is only been done once. The waste water of acid dyeing is treated via membrane filtration and reused for acid  dyeing. The waste water of these treatments has not been treated and tested for reuse. It is to be expected that several reuse cycles will generate a higher concentration of certain chemicals in the permeate. To prevent this increase in concentration it is better to mix the permeate with fresh process water. In any case extra fresh process water is needed since part of the water is taken up by the fabric and is lost by evaporation.

#### Reuse of acid dyeing effluent (silk dyeing)

The permeate of acid dyeing has been reused for degumming and acid dyeing of silk both in a light and a dark colour shade.

##### Degumming efficiency

| TYPE OF TREATMENT | DEGREE OF WHITE | x | y | Y |
| --- | --- | --- | --- | --- |
| REFERENCE | 53.6 | 0.3215 | 0.3393 | 73.9 |
| REUSE | 54.1 | 0.3214 | 0.3391 | 73.9 |

The variations in the values of the degree of white in the silk samples scoured with two water types, is irrelevant.

##### Colour differences

| Formula: CMC 2.0:1.0 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Substratum: fabric 100% silk |  |  |  |  |  |
| Reference: COL. BROWN- DYE WITH INDUSTRIAL WATER |  |  |  |  |  |
| Sample: COL. BROWN-DYE WITH TREATED WATER |  |  |  |  |  |
|  | delE | delL | delC | delH | the sample is |
| D65/10 | 0.581 | 0.564 | -0.101 | 0.096 | + clear + dirty |
| A/10 | 0.561 | 0.548 | -0.111 | 0.048 | + clear + dirty |
| F11/10 | 0.565 | 0.558 | -0.085 | 0.023 | + clear |
| Formula: CMC 2.0:1.0 |  |  |  |  |  |
| Substratum: 100% silk fabric |  |  |  |  |  |
| Reference: COL. GREEN– DYE WITH INDUSTRIAL WATER |  |  |  |  |  |
| Sample: COL. GREEN – DYE WITH TREATED WATER |  |  |  |  |  |
|  | delE | delL | delC | delH | the sample is |
| D65/10 | 0.664 | -0.546 | 0.249 | 0.286 | + dark+ pure + green |
| A/10 | 0.746 | -0.586 | 0.192 | 0.420 | + dark + pure + green |
| F11/10 | 0.667 | -0.583 | 0.118 | 0.302 | + dark + pure + green |

The variations of tone between the samples dyed in the two types of water are within the acceptable levels of tolerance as recommended in the quality standard norm of the 2003 edition of Italian Textile Association. ( i.e.: delE=1)

##### Colour fastness to washing

Brown:

|  | dyeing in industrial water | dyeing in treated water |
| --- | --- | --- |
| Degradation colour: | 2 | 2 |
| Staining on: |  |  |
| Wool | 1-2 | 2 |
| Acrylic | 3/4 | 4 |
| Polyester | 3 | 3-4 |
| Polyamide | 1 | 1 |
| Cotton | 1 | 1-2 |
| Acetate | 3 | 3-4 |

Green:

|  | dyeing in industrial water | dyeing in treated water |
| --- | --- | --- |
| Degradation colour: | 3 | 3 |
| Staining on: |  |  |
| Wool | 3 | 2-3 |
| Acrylic | 4-5 | 4 |
| Polyester | 4 | 4 |
| Polyamide | 2 | 1/2 |
| Cotton | 3-4 | 3-4 |
| Acetate | 4 | 4 |

The differences in colour fastness expressed are not significant.

##### Colour fastness to rubbing

| dyeing in industrial water |  | dyeing in treated water |  |
| --- | --- | --- | --- |
| Colour fastness to rubbing |  | Colour fastness to rubbing |  |
| dry | wet | dry | wet |
| Brown |  |  |  |
| 4-5 | 4-5 | 4-5 | 4-5 |
| Green |  |  |  |
| 4-5 | 4 | 4-5 | 4 |

As outlined there is no variation between colour fastness to rubbing in the samples dyed in using two types of water.

##### Conclusions: reuse of permeate for degumming and acid dyeing of silk

In general the differences revealed at the end of each test is of little significance as they do not indicate any particular problem.

The results obtained with treated water, in reference to the materials used in the  laboratory can be considered equal to those obtained by using industrial water.

## Reactive dyeing and printing(Viscose printed washing, Silk yarn dyeing and Cotton dyeing)

In the present chapter, discussion and results of the experimental activities carried out on the two acid dyeing effluents is reported. In the table below, the treatments carried out on each effluent is synthesized:

| Process Effluent | UF | NF | UF+NF | Anaer.+ UF | Anaer+ NF | Anaer +UF+NF |
| --- | --- | --- | --- | --- | --- | --- |
| Viscose reactive printed wash (VRPW) | X | X | X |  |  |  |
| Silk yarn reactive dyeing (SYRD) | X |  | X |  |  |  |
| Cotton reactive dyeing (CRD) | X |  | X | X | X | X |

### Anaerobic tests results (Cotton Dyeing)

Results of the experiment are represented at three different wavelengths. The wastewater contains three dyes, and the wavelengths are chosen to try to represent the three colours: yellow (420 nm), red (500 nm) and blue (620 nm).

#### Results of batch experiments

Figure 59 shows the mesophilic experiment, during the complete treatment time, for absorption at 500 nm (the main maximum absorption wavelength for the wastewater). The UV-VIS spectra of the reactive dyeing incubations at different time intervals can be found in Appendix D.

Figure 59 - Decolourisation (measured at 500 nm) of reactive dyeing wastewater at 30C. ♦ = chemical control, ● = sludge + w.w., x = sludge + w.w. + AQS, Δ = sludge + w.w. + size, □ = sludge + w.w. + size + AQS, ▲ = sludge + w.w. + VFA-Glucose, ■ = sludge + w.w. + VFA-Glucose + AQS.

##### Meso- and thermophilic decolourisation with VFA-Glucose as cosubstrate

The results of the experiment are presented in Figure 60, in three different graphs. Each graph representing a different wavelength. At all three wavelengths the chemical control shows distinctively lower decolourisation rates. Colour removal is clearly a biological process, as the addition of co-substrate stimulates the decolourisation rates. In comparison to mesophilic conditions, thermophilic conditions speed up the process.

##### Effect of AQS on meso and thermophilic decolourisation with VFA-Glucose

Electron mediating compounds have proven to speed up decolourisation rates for azo dyes (van der Zee et al., 2003). Practically all research on mediators has been done with single-dye systems, which makes this experiment one of the first with real textile wastewater. Another fairly unexplored area is the use of electron mediators in thermophilic systems. In Figure 61 the results are shown. It can be seen that the addition of an electron mediator increases decolourisation rates, especially under mesophilic conditions. Apparently, thermophilic conditions already lead to such an increase that the mediator can not speed it up much more. For the measurements at 610 nm there is practically no difference in decolourisation rates. Neither between the batches with and without AQS, nor between the mesophilic and the thermophilic batches. However, there is a difference in the maximum decolourisation obtained: thermophilic treatment renders a better end result.

##### Decolourisation with size as cosubstrate in presence and absence of AQS

This experiment was conducted only at 30C. The results for size as a cosubstrate (Figure 62) do not differ a lot from the results obtained with VFA-Glucose.

##### Comparison of co-substrates and AQS concentration

When comparing the three types of incubations, a difference can be seen between the graphs at different wavelengths. At 420 nm the incubations with 0.05 mM AQS do not really differ from the ones without AQS. The higher amount of AQS has a clearly visible impact. For the graph at 500 nm, all three incubations are different, the small amount of AQS has a small impact. Looking at the graph of 600 nm, no difference can be observed between the incubations, AQS does not speed up decolourisation.

Light absorbed at a different wavelength, makes that we see it as a colour. Dyes are molecules that are designed to absorb at a certain wavelength, to result in a certain colour. In dyebaths, usually three dyes are present, a yellow one, a red one and a blue one. When choosing three wavelengths in those colour regions, each wavelength should represent one of the three dyes in the wastewater. The differences in decolourisation between the three wavelengths mean that each dye reacts differently to the mediator.

| 420 nm |  | 420 nm |
| --- | --- | --- |
| 500 nm |  | 500 nm |
| 610 nm |  | 610 nm |
| Figure 60 - Decolourisation of reactive dyeing wastewater in presence and absence of co-substrate at 30C (open symbols) and 55C (filled symbols). ◊ = chemical control, o = sludge + wastewater (w.w.), Δ = sludge + w.w. + VFA/glucose as cosubstrate. |  | Figure 61 – Decolourisation of reactive dyeing wastewater in presence and absence of 0.5 mM AQS at 30C (open symbols) and 55C (filled symbols). ◊ = chemical control, o = sludge + w.w. + AQS, Δ = sludge + w.w. + VFA/glucose, □ = sludge + w.w. + VFA/glucose + AQS. |

| 420 |  | 420 |
| --- | --- | --- |
| 500 |  | 500 |
| 610 |  | 610 |
| Figure 62 – Decolourisation of reactive dyeing wastewater with size, in presence and absence of 0.5 mM AQS at 30C. ◊ = chemical control, o = sludge + w.w., x = sludge + w.w. + AQS, Δ = sludge + w.w. + size, □ = sludge + w.w. + size + AQS. |  | Figure 63 – Decolourisation of reactive dyeing wastewater with size (filled symbols) or VFA-glucose (open symbols), in presence and absence of 0.5 or 0.05 mM AQS at 30C. Δ = sludge + w.w. + cosubstrate, o = sludge + w.w. + cosubstrate + 0.05 mM AQS, □ = sludge + w.w. + cosubstrate + 0.5 mM AQS. |

#### Results of the continuous experiment

The goal of the continuous experiment with reactive dyeing wastewater was first of all to investigate the potential of anaerobic treatment as a pre-treatment step before membrane filtration (see Introduction). The amount of wastewater chosen was quite small, based on the amount needed by ENEA to perform a filtration delivering enough permeate for Centexbel to do reuse tests. First an attempt was made to treat the wastewater without addition of a co-substrate. After some days it was decided to add sizing liquid, a textile waste-stream rich in starch. When all the wastewater was treated, the collected effluent was used as influent again. This was based on the assumption that the effluent collected in the first days of the experiment had a higher residual colour than the latest collected effluent. In this way the whole effluent would get the same “level” of treatment. Figure 64 gives the results for decolourisation, methane production and COD-removal.

Figure 64 - Continuous experiment with reactive dyeing wastewater in an EGSB-type reactor.  = 420 nm, ■ = 500 nm, ▲ = 620 nm, o = methane production, ● = COD removal.

The first vertical line indicates the change of wastewater to wastewater with size added as co-substrate, the second line the feeding of the collected effluent as influent after finishing the wastewater. As can be seen in Figure 64, adding a co-substrate to the wastewater increased the colour removal. Decolourisation was constant at the three wavelengths. COD removal and methane production were constant until day 15. After that day, both started dropping fast although colour removal remained the same. Apparently the wastewater affects the reactor on the long term. When the reactor is fed with its own effluent, the measured colour removal drops, probably due to the same what made COD removal and CH4 production fall down. However, the visible colour of the effluent diminished after feeding it to the reactor a second time (see Figure 65).

Figure 65 - Visible colour of the reactive dyeing influent and its two consecutive effluents. Left: reactive dyeing influent, middle: first effluent (sample day 20), right: effluent after treatment of the first effluent (sample day 30).

### Membrane treatment results

#### Direct NF results

Direct nanofiltration has been applied on VRPW effluent. The results of the tests carried out according to the methods described above, on bench scale and on pilot scale are here reported.

##### Bench scale NF on VRPW effluent

###### Characterization of VRPW/NF

Flow rate measurements at 6 bar pressure for three membranes at constant temperature (25 °C):

| P 6 bar | Membrane | Q25 [ l ·h-1·m-2 ] |
| --- | --- | --- |
|  | DK | 57 |
|  | DL | 69 |
|  | HL | 51 |

###### Complete recirculation test of VRPW/NF

Flow rate decrease passing to real effluent filtration:

| P 6 bar | Membrane | Q25 [ l · h-1· m-2 ] | Flow rate decrease [%] |
| --- | --- | --- | --- |
|  | DK | 42 | 26 |
|  | DL | 54 | 22 |
|  | HL | 43 | 17 |

Permeates quality:

|  | Feed | 15' DK | 15' DL | 15' HL |
| --- | --- | --- | --- | --- |
| PH | 9.25 | 9.84 | 9.74 | 9.88 |
| Conductivity [S·cm-1] | 1196 | 341 | 170 | 177 |
| Turbidity [NTU] | 1.3 | 0.64 | 0.62 | 0.75 |
| Abs  = 426 nm | 0.379 | 0.016 | 0.011 | 0.010 |
| Abs  = 558 nm | 0.315 | 0.011 | 0.012 | 0.007 |
| Abs  = 660 nm | 0.143 | 0.006 | 0.003 | 0.003 |
| Abs  = 436 nm | 0.374 | 0.013 | 0.010 | 0.009 |
| Abs  = 525 nm | 0.367 | 0.011 | 0.012 | 0.007 |
| Abs  = 620 nm | 0.224 | 0.008 | 0.006 | 0.005 |
| TOC [mg · l-1] | 716.2 | 386.3 | 232.3 | 285.0 |
| TC [mg · l-1] | 725.0 | 402.9 | 242.3 | 298.4 |
| IC [mg · l-1] | 8.810 | 16.60 | 10.00 | 13.37 |

###### Choice of the membrane for the pilot scale

The decrease of flow rate passing from deionised water to real effluent filtration is high for all the three membranes. DL has the highest flow rate.

Membrane DK and HL have better removal efficiency on salinity, organic carbon content in reference to DL, nevertheless DL is chosen for further investigation.

##### Pilot scale NF on VRPW effluent

###### Pi. Sc. characterization of VRPW/NF

Flow rates at different pressure values:

| P [ bar ] | Q30 [ l · h-1] | Q34 [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 6 | 23 | 26 | 21 |
| 6.9 | 26 | 28 | 23 |
| 9 | 33 | 36 | 30 |

###### Pi. Sc. complete recirculation test of VRPW/NF

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 31 | 23 | 20 |
| 15 | 32 | 23 | 20 |
| 30 | 33 | 24 | 20 |
| 45 | 34 | 25 | 21 |
| 60 | 35 | 26 | 21 |

|  | Feed | permeate 0' | permeate 60' |
| --- | --- | --- | --- |
| pH | 9.4 | 10 | 9.9 |
| Conductivity [S·cm-1] | 1223 | 204 | 215 |
| Turbidity [NTU] | 2.6 | 1.3 | 0.7 |
| Abs  = 426 nm | 0.393 | 0.008 | 0.018 |
| Abs  = 558 nm | 0.33 | 0.007 | 0.014 |
| Abs  = 660 nm | 0.153 | 0.004 | 0.006 |
| Abs  = 436 nm | 0.388 | 0.006 | 0.016 |
| Abs  = 525 nm | 0.383 | 0.005 | 0.015 |
| Abs  = 620 nm | 0.238 | 0.006 | 0.009 |
| TOC [mg · l-1] | 700 | 371 | 358 |
| TC [mg · l-1] | 740 | 381 | 366 |
| IC [mg · l-1] | 39 | 10 | 8 |

###### Concentration effect test of VRPW/NF

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 32 | 23 | 20 |
| 20 | 33 | 23 | 20 |
| 40 | 33 | 23 | 20 |
| 60 | 34 | 22 | 18 |
| 80 | 35 | 20 | 16 |

|  | Feed | perm. 0% | perm. 20% | perm. 40% | perm. 60% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 9.4 | 9.8 | 9.8 | 9.6 | 9.4 | 9.2 | 8.9 |
| Conductivity [S·cm-1] | 1223 | 222 | 280 | 383 | 570 | 1077 | 4670 |
| Turbidity [NTU] | 2.6 | 1.0 | 0.6 | 0.9 | 0.3 | 0.5 | 2.1 |
| Abs  = 426 nm | 0.393 | 0.015 | 0.015 | 0.010 | 0.010 | 0.011 | 2.160 |
| Abs  = 558 nm | 0.330 | 0.011 | 0.010 | 0.007 | 0.003 | 0.001 | 1.839 |
| Abs  = 660 nm | 0.153 | 0.007 | 0.005 | 0.005 | 0.001 | 0.000 | 0.791 |
| Abs  = 436 nm | 0.388 | 0.013 | 0.013 | 0.008 | 0.008 | 0.008 | 2.134 |
| Abs  = 525 nm | 0.383 | 0.010 | 0.011 | 0.004 | 0.002 | 0.001 | 2.213 |
| Abs  = 620 nm | 0.238 | 0.010 | 0.008 | 0.007 | 0.003 | 0.001 | 1.258 |
| TOC [mg · l-1] | 700 | 360 | 362 | 374 | 388 | 524 | 1953 |
| TC [mg · l-1] | 740 | 372 | 383 | 402 | 429 | 577 | 2119 |
| IC [mg · l-1] | 39 | 12 | 21 | 28 | 40 | 53 | 166 |

♦ TOC in the feed

■ TOC in the permeate

###### Second characterization of VRPW/NF

Flow rates in the second characterization and comparison among first, second and after washing characterization:

| p [ bar ] | Q30 [ l · h-1] | Q34 [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 6 | 20 | 22 | 18 |
| 6.9 | 23 | 25 | 21 |
| 9 | 30 | 32 | 27 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % | Q25 after washing. [ l · h-1] | Loss % |
| --- | --- | --- | --- | --- | --- |
| 6 | 21 | 18 | 14 | 21 | 0 |
| 6.9 | 23 | 21 | 9 | 23 | 0 |
| 9 | 30 | 27 | 10 | 31 | 0 |

###### Conclusions of VRPW/NF

A slight decrease in flow rate was observed passing from pure water to real effluent showing a quite good affinity.

At increasing concentration a relevant effect was noticed only above the 60% increase in concentration of the feed.

The quality of the permeate is low, not acceptable for reuse tests. In particular the organic content is high in the effluent. Colour is removed almost completely.

Comparison among flow rates measured in all the pilot scale trials:

Quality of the aver. permeate and percentage abatement:

|  | Feed | Permeate | Abatement % |
| --- | --- | --- | --- |
| pH | 9.4 | 9.6 | - |
| Conductivity [S·cm-1] | 1223 | 506 | 59 |
| Turbidity [NTU] | 2.6 | 0.66 | 75 |
| Abs  = 426 nm | 0.393 | 0.012 | 97 |
| Abs  = 558 nm | 0.33 | 0.006 | 98 |
| Abs  = 660 nm | 0.153 | 0.004 | 98 |
| Abs  = 436 nm | 0.388 | 0.010 | 97 |
| Abs  = 525 nm | 0.383 | 0.006 | 99 |
| Abs  = 620 nm | 0.238 | 0.006 | 98 |
| TOC [mg · l-1] | 700 | 402 | 43 |
| TC [mg · l-1] | 740 | 433 | 42 |
| IC [mg · l-1] | 39 | 31 | 22 |

#### UF results

##### Pilot scale UF on VRPW effluent

UF membrane choice was performed on the base of previous experimental results. Membrane labelled MW, produced by Osmonics Inc. was selected. Investigation was carried out on pilot scale.

###### Pi. Sc. characterization of VRPW/UF

Flow rates at different pressure and temperature values:

| p [ bar ] | Q25 [ l · h-1] | Q27 [ l · h-1] | Q30 [ l · h-1] |
| --- | --- | --- | --- |
| 1.4 | 35 | 36 | 36 |
| 1.9 | 45 | 45 | 47 |
| 2.3 | 53 | 53 | 53 |
| 2.8 | 60 | 60 | 64 |

###### Pi. Sc. complete recirculation test of VRPW/UF

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 24 | 43 | 43 |
| 15 | 25 | 43 | 43 |
| 30 | 26 | 45 | 45 |
| 45 | 26 | 43 | 43 |
| 60 | 27 | 43 | 43 |

|  | Feed | permeate 0' | permeate 60' |
| --- | --- | --- | --- |
| pH | 9.3 | 9.5 | 9.4 |
| Conductivity [S·cm-1] | 759 | 587 | 584 |
| Turbidity [NTU] | 1.5 | 0.8 | 0.3 |
| Abs  = 426 nm | 0.272 | 0.075 | 0.071 |
| Abs  = 558 nm | 0.22 | 0.039 | 0.036 |
| Abs  = 660 nm | 0.103 | 0.012 | 0.011 |
| Abs  = 436 nm | 0.27 | 0.076 | 0.072 |
| Abs  = 525 nm | 0.263 | 0.062 | 0.057 |
| Abs  = 620 nm | 0.151 | 0.018 | 0.017 |
| TOC [mg · l-1] | 462 | 361 | 359 |
| TC [mg · l-1] | 502 | 364 | 366 |
| IC [mg · l-1] | 40 | 3 | 7 |

###### Concentration effect test of VRPW/UF

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 26 | 43 | 43 |
| 20 | 26 | 41 | 41 |
| 40 | 27 | 41 | 40 |
| 60 | 27 | 38 | 37 |
| 80 | 28 | 34 | 33 |

|  | Feed | perm. 0% | perm. 20% | perm. 40% | perm. 60% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 9.3 | 9.3 | 9.4 | 9.4 | 9.4 | 9.3 | 9.2 |
| Conductivity [S·cm-1] | 759 | 596 | 610 | 641 | 698 | 773 | 1126 |
| Turbidity [NTU] | 1.5 | 0.6 | 0.6 | 0.5 | 0.6 | 0.5 | 2.5 |
| SST [mg · l-1] | 0.272 | 0.082 | 0.083 | 0.099 | 0.151 | 0.228 | 0.779 |
| Abs  = 426 nm | 0.220 | 0.046 | 0.044 | 0.056 | 0.096 | 0.155 | 0.726 |
| Abs  = 558 nm | 0.103 | 0.016 | 0.014 | 0.016 | 0.033 | 0.053 | 0.345 |
| Abs  = 660 nm | 0.270 | 0.082 | 0.084 | 0.100 | 0.150 | 0.227 | 0.765 |
| Abs  = 436 nm | 0.263 | 0.069 | 0.069 | 0.085 | 0.135 | 0.210 | 0.805 |
| Abs  = 525 nm | 0.151 | 0.023 | 0.021 | 0.026 | 0.048 | 0.080 | 0.531 |
| Abs  = 620 nm | 462 | 375 | 372 | 378 | 384 | 389 | 931 |
| TOC [mg · l-1] | 502 | 378 | 375 | 380 | 385 | 397 | 971 |
| TC [mg · l-1] | 40 | 3 | 3 | 2 | 1 | 7 | 40 |
| IC [mg · l-1] | 9.3 | 9.3 | 9.4 | 9.4 | 9.4 | 9.3 | 9.2 |

♦ TOC in the feed

■ TOC in the permeate

###### Second characterization of VRPW/UF

Flow rates in the second characterization and comparison between first and second characterization:

| p [ bar ] | Q25 [ l · h-1] | Q27 [ l · h-1] | Q30 [ l · h-1] |
| --- | --- | --- | --- |
| 1.4 | 38 | 41 | 41 |
| 1.9 | 47 | 50 | 53 |
| 2.3 | 56 | 60 | 62 |
| 2.8 | 64 | 69 | 75 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 1.9 | 45 | 47 | -4 |
| 2.3 | 53 | 56 | -6 |

###### Conclusions of VRPW/UF

The affinity membrane/real effluent is quite good as observable by the slight decrease in flow rate.

A remarkable loss in flow rate is observed during the concentration effect test but a complete recovery of the initial flow rate is obtained with the second characterization.

The quality of permeates is not very good due to the high content of organics and colour compounds in the effluent because of the low removal

Comparison among flow rates measured in all the pilot scale trials:

Quality of the aver. permeate and percentage abatement:

The permeate effluent from ultrafiltration is submitted to nanofiltration as described in § 4.7.2.3.1

|  | Feed | Permeate UF | Abatement % |
| --- | --- | --- | --- |
| pH | 9.3 | 9.4 | - |
| Conductivity [S·cm-1] | 759 | 663.6 | 13% |
| Turbidity [NTU] | 1.5 | 0.542 | 64% |
| Abs  = 426 nm | 0.272 | 0.129 | 53% |
| Abs  = 558 nm | 0.220 | 0.079 | 64% |
| Abs  = 660 nm | 0.103 | 0.026 | 74% |
| Abs  = 660 nm | 0.270 | 0.129 | 52% |
| Abs  = 660 nm | 0.263 | 0.114 | 57% |
| Abs  = 660 nm | 0.151 | 0.040 | 74% |
| TOC [mg · l-1] | 462 | 379.7 | 18% |
| TC [mg · l-1] | 502 | 383.0 | 24% |
| IC [mg · l-1] | 40 | 3.3 | 92% |

##### Bench scale UF on SYRD effluent

###### Characterization of SYRD/UF

Flow rate measurements at 6 bar pressure for three membranes at constant temperature (25 °C):

| P |  | ER |  |  |  | PW |  |  |  |  | GK |  |  |  |  | GH |  |  |  |  | MW |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | T (°C) |  | Q (l h-1 m-2) |  | T (°C) |  | Q (l h-1 m-2) |  |  | T (°C) |  | Q (l h-1 m-2) |  |  | T (°C) |  | Q (l h-1 m-2) |  |  | Q (l h-1) |  | Q (l h-1 m-2) |
| 1 |  |  |  |  |  | 26 |  | 228 |  |  |  |  |  |  |  |  |  |  |  | 25 |  |  | 290 |  |
| 1.5 |  |  |  |  |  | 26 |  | 332 |  |  |  |  |  |  |  |  |  |  |  | 25 |  |  | 415 |  |
| 2 |  | 27 |  | 153 |  | 26 |  | 430 |  | 27 |  |  | 13 |  |  |  |  |  |  | 25 |  |  | 553 |  |
| 2.5 |  | 26 |  | 197 |  | 26 |  | 528 |  | 27 |  |  | 18 |  |  |  |  |  |  | 25 |  |  | 726 |  |
| 3 |  | 26 |  | 235 |  |  |  |  |  | 26 |  |  | 20 |  |  |  |  |  |  |  |  |  |  |  |
| 3.5 |  | 25 |  | 264 |  |  |  |  |  | 25 |  |  | 22 |  |  |  |  |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 4.5 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 28 |  |  | 15 |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 27 |  |  | 16 |  |  |  |  |  |  |
| 5.5 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 25 |  |  | 16 |  |  |  |  |  |  |

###### Complete recirculation test of SYRD/UF

Flow rate decrease passing to real effluent filtration:

| Membrane | P (bar) | T (°C) | QT [ l · h-1· m-2 ] | Flow rate decrease [%] |
| --- | --- | --- | --- | --- |
| ER | 3.4 | 21 | 26 | 90 |
| MW | 2.1 | 24 | 124 | 71 |
| PW | 2.1 | 24 | 79 | 86 |

K=0.008

Permeates quality:

|  | Feed | ER | MW | PW |
| --- | --- | --- | --- | --- |
| pH | 9.5 | 9.5 | 9.5 | 9.5 |
| Conductivity [S·cm-1] | 39.800 | 98.800 | 39.000 | 39.300 |
| Turbidity [NTU] | 0.5 | 0.7 | 0.4 | 1.1 |
| SST (mg l-1) | 41 | - | - | - |
| Abs  = 426 nm | 2.811 | 1.049 | 1.863 | 1.458 |
| Abs  = 558 nm | 3.932 | 2.722 | 3.712 | 3.434 |
| Abs  = 660 nm | 0.030 | 0.019 | 0.023 | 0.022 |
| TOC [mg · l-1] | 758 | 299 | 571 | 342 |
| TC [mg · l-1] | 1500 | 989 | 1281 | 1051 |
| IC [mg · l-1] | 742 | 689 | 710 | 709 |

###### Choice of the membrane for the pilot scale

The highest flow rate among the membrane tested was obtained by membrane MW followed by ER (even if the operational pressure is higher). The values obtained for PW are very low. Comparing these flows with the ones obtained during the characterization in all cases the loss is relevant (due to the unexpectedly high values measured in characterization). With referencxe to this parameter, ER is slightly better than MW and PW.

All the membrane have evidenced almost total removal of colour, suspended solids and turbidity. Membrane MW leaves in the permeates a residual organic content and conductivity significantly higher. All this considered, being UF mainly a pre-treatment in this case, the hydraulic parameters are evaluated as most important therefore MW is chosen for further investigation.

##### Pilot scale UF on SYRD effluent

###### Pi. Sc. characterization of SYRD/UF

Flow rates at different pressure and 32 °C temperature values:

| p [ bar ] | Q32 [ l · h-1] |
| --- | --- |
| 1.4 | 40 |
| 1.9 | 49 |
| 2.3 | 58 |
| 2.8 | 68 |

###### Pi. Sc. complete recirculation test of SYRD/UF

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 14 | 29 | 32 |
| 15 | 16 | 28 | 30 |
| 30 | 18 | 27 | 29 |
| 45 | 20 | 26 | 27 |
| 60 | 21 | 26 | 27 |

|  | Feed | Permeate 0’ | Permeate 60’ |
| --- | --- | --- | --- |
| pH | 9.5 | 9.5 | 9.5 |
| Conductivity [S·cm-1] | 39800 | 34300 | 35900 |
| Turbidity [NTU] | 0.4 | 1.3 | 0.7 |
| SST (mg l-1) | 39 | - | - |
| Abs  = 426 nm | 2.813 | 2.100 | 1.899 |
| Abs  = 558 nm | 3.939 | 3.772 | 3.703 |
| Abs  = 660 nm | 0.022 | 0.027 | 0.024 |
| TOC [mg · l-1] | 775 | 490 | 420 |
| TC [mg · l-1] | 1528 | 1108 | 1056 |
| IC [mg · l-1] | 753 | 618 | 636 |

###### Concentration effect test of SYRD/UF

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 20 | 31 | 32 |
| 20 | 20 | 28 | 29 |
| 40 | 21 | 24 | 25 |
| 60 | 22 | 26 | 26 |
| 80 | 22 | 26 | 26 |

|  | Feed | perm. 0% | perm. 20% | perm. 40% | perm. 60% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 |
| Conductivity [S·cm-1] | 39800 | 35800 | 35800 | 35900 | 36000 | 35800 | 35900 |
| Turbidity [NTU] | 0.4 | 1.7 | 0.3 | 0.6 | 0.7 | 1.0 | 0.4 |
| SST (mg l-1) | 39 | 37 | 31 | 33 | 37 | 39 | 35 |
| Abs  = 426 nm | 2.813 | 2.102 | 1.944 | 1.965 | 2.041 | 2.195 | 3.431 |
| Abs  = 558 nm | 3.939 | 3.770 | 3.738 | 3.762 | 3.813 | 3.883 | 4.034 |
| Abs  = 660 nm | 0.022 | 0.024 | 0.015 | 0.023 | 0.022 | 0.025 | 0.039 |
| TOC [mg · l-1] | 775 | 456 | 422 | 433 | 447 | 460 | 1175 |
| TC [mg · l-1] | 1529 | 1089 | 1069 | 1070 | 1071 | 1094 | 1805 |
| IC [mg · l-1] | 753 | 633 | 647 | 637 | 624 | 634 | 630 |

♦ TOC in the feed

■ TOC in the permeate

###### Second characterization of SYRD/UF

Flow rates in the second characterization and comparison between first and second characterization:

| p [ bar ] | Q32 [ l · h-1] |
| --- | --- |
| 1.4 | 38 |
| 1.9 | 48 |
| 2.3 | 46 |
| 2.8 | 64 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 2.1 | 51 | 49 | 4 |

###### Conclusions of SYRD/UF

The loss in flow rate passing from water filtering to real effluent is quite high showing poor affinity, followed by a significant effect due to increasing concentration.

A good recovery of flow rate is observed in the second characterization.

The quality of the permeate does not allow for reuse options due to the low removals performed by the ultrafiltration.

Comparison among flow rates measured in all the pilot scale trials:

|  | Feed | Permeate UF | Abatement % |
| --- | --- | --- | --- |
| pH | 9.5 | 9.5 |  |
| Conductivity [S·cm-1] | 39800 | 35860 | 10% |
| Turbidity [NTU] | 0.4 | 0.9 | -143% |
| SST (mg l-1) | 39 | 35.4 | 9% |
| Abs  = 426 nm | 2.813 | 2.049 | 27% |
| Abs  = 558 nm | 3.939 | 3.793 | 4% |
| Abs  = 660 nm | 0.022 | 0.022 | 1% |
| TOC [mg · l-1] | 775 | 443.5 | 43% |
| TC [mg · l-1] | 1529 | 1078.4 | 29% |
| IC [mg · l-1] | 753 | 634.9 | 16% |

The permeate effluent from ultrafiltration is submitted to two nanofiltrations (2 membranes) as described in § 4.7.2.3.3. e 4.7.2.3.4.

##### Pilot scale UF on CRD effluent

UF membrane choice was performed on the base of previous experimental results. Membrane labelled MW, produced by Osmonics Inc. was selected. Investigation was carried out on pilot scale

###### Pi. Sc. characterization of CRD/UF

Flow rates at different pressure and temperature values:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 1.4 | 38 |
| 1.9 | 48 |
| 2.3 | 56 |
| 2.8 | 62 |

###### Pi. Sc. complete recirculation test of CRD/UF

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 20 | 43 | 45 |
| 20 | 20 | 42 | 44 |
| 40 | 20 | 41 | 43 |
| 60 | 21 | 40 | 41 |

|  | Feed | permeate 0' | permeate 60' |
| --- | --- | --- | --- |
| pH | 9.9 | 9.9 | 9.9 |
| Conductivity [S·cm-1] | 16800 | 17060 | 17090 |
| Abs  = 426 nm | 0.466 | 0.397 | 0.379 |
| Abs  = 558 nm | 0.355 | 0.303 | 0.283 |
| Abs  = 660 nm | 0.151 | 0.121 | 0.114 |
| Abs  = 436 nm | 0.464 | 0.396 | 0.378 |
| Abs  = 525 nm | 0.363 | 0.313 | 0.290 |
| Abs  = 620 nm | 0.345 | 0.291 | 0.277 |
| TOC [mg · l-1] | 120 | 69 | 64 |
| TC [mg · l-1] | 370 | 319 | 312 |
| IC [mg · l-1] | 250 | 250 | 248 |

###### Concentration effect test of CRD/UF

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 20 | 40 | 42 |
| 40 | 21 | 39 | 40 |
| 80 | 21 | 38 | 39 |

|  | Feed | perm. 0% | perm. 40% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- |
| pH | 9.9 | 9.9 | 9.9 | 9.9 | 10.0 |
| Conductivity [S·cm-1] | 16800 | 17090 | 17080 | 17130 | 17076 |
| TOC [mg · l-1] | 120 | 64 | 62 | 72 | 162 |
| TC [mg · l-1] | 370 | 312 | 308 | 322 | 408 |
| IC [mg · l-1] | 250 | 248 | 246 | 250 | 246 |
| Abs  = 426 nm | 0.466 | 0.379 | 0.429 | 0.452 | 0.564 |
| Abs  = 558 nm | 0.355 | 0.283 | 0.322 | 0.342 | 0.438 |
| Abs  = 660 nm | 0.151 | 0.114 | 0.137 | 0.142 | 0.206 |
| Abs  = 436 nm | 0.464 | 0.378 | 0.428 | 0.451 | 0.562 |
| Abs  = 525 nm | 0.363 | 0.29 | 0.331 | 0.354 | 0.443 |
| Abs  = 620 nm | 0.345 | 0.277 | 0.313 | 0.33 | 0.438 |
| SST [mg · l-1] | 18.5 | - | - | - | 15.6 |

###### Second characterization of CRD/UF

Flow rates in the second characterization and comparison between first and second characterization:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 1.4 | 38 |
| 1.9 | 47 |
| 2.3 | 54 |
| 2.8 | 62 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 2.1 | 52 | 51 | 2% |

###### Conclusions of CRD/UF

The affinity shown by the effluent for the membrane is quite good and similar behaviour is performed during the concentration effect test and in the second characterization.

The reuse is escluded due to high conductivity and color in the effluent. In fact, the removals performed on these parameters are very low.

Comparison among flow rates measured in all the pilot scale trials.

Comparison among flow rates measured in all the pilot scale trials

|  | Feed | Permeate UF | Abatement % |
| --- | --- | --- | --- |
| pH | 9.9 | 9.9 |  |
| Conductivity [S·cm-1] | 16800 | 17100 | -2% |
| TOC [mg · l-1] | 120 | 66 | 45% |
| TC [mg · l-1] | 370 | 314 | 15% |
| IC [mg · l-1] | 250 | 248 | 1% |
| Abs  = 426 nm | 0.466 | 0.420 | 10% |
| Abs  = 558 nm | 0.355 | 0.316 | 11% |
| Abs  = 460 nm | 0.151 | 0.131 | 13% |
| Abs  = 436 nm | 0.464 | 0.419 | 10% |
| Abs  = 525 nm | 0.363 | 0.325 | 10% |
| Abs  = 620 nm | 0.345 | 0.307 | 11% |
| SST (mg l-1) | 18.5 |  | >99% |

The permeate effluent from ultrafiltration is submitted to nanofiltration as described in § 4.7.2.3.5.

#### UF +NF results

##### Pilot scale NF on VRPW after UF

###### Pi. Sc. characterization of VRPW/NF

Flow rates at different pressure values:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 6 | 21 |
| 6.9 | 23 |
| 9 | 31 |

###### Pi. Sc. complete recirculation test of VRPW /NF

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 27 | 15 | 14 |
| 15 | 29 | 17 | 16 |
| 30 | 30 | 18 | 16 |
| 45 | 31 | 19 | 17 |
| 60 | 31 | 20 | 18 |

|  | Feed | permeate 0' | permeate 60' |
| --- | --- | --- | --- |
| pH | 9.4 | 10.4 | 10.4 |
| Conductivity [S·cm-1] | 664 | 124 | 132 |
| Turbidity (NTU) | 0.5 | 0.6 | 0.4 |
| Abs  = 426 nm | 0.129 | 0.004 | 0.003 |
| Abs  = 558 nm | 0.079 | 0.002 | 0.002 |
| Abs  = 660 nm | 0.026 | 0.003 | 0.000 |
| Abs  = 436 nm | 0.129 | 0.003 | 0.003 |
| Abs  = 525 nm | 0.114 | 0.001 | 0.002 |
| Abs  = 620 nm | 0.040 | 0.003 | 0.001 |
| TOC [mg · l-1] | 380 | 302 | 295 |
| TC [mg · l-1] | 383 | 279 | 280 |
| IC [mg · l-1] | 3 | 0 | 1 |

###### Concentration effect test of VRPW/NF

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 31 | 20 | 18 |
| 20 | 32 | 20 | 17 |
| 40 | 33 | 20 | 17 |
| 60 | 33 | 20 | 17 |
| 80 | 34 | 19 | 16 |

|  | Feed | perm. 0% | perm. 20% | perm. 40% | perm. 60% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 9.4 | 10.2 | 9.9 | 9.9 | 9.4 | 9.6 | 10.0 |
| Conductivity [S·cm-1] | 664 | 131 | 156 | 201 | 300 | 522 | 1120 |
| Turbidity [NTU] | 0.5 | 0.9 | 0.7 | 0.8 | 0.3 | 0.2 | 0.6 |
| Abs  = 426 nm | 0.129 | 0.004 | 0.005 | 0.005 | 0.004 | 0.005 | 0.228 |
| Abs  = 558 nm | 0.079 | 0.002 | 0.003 | 0.003 | 0.001 | 0.001 | 0.140 |
| Abs  = 660 nm | 0.026 | 0.001 | 0.002 | 0.001 | 0.000 | 0.001 | 0.045 |
| Abs  = 436 nm | 0.129 | 0.004 | 0.005 | 0.005 | 0.003 | 0.003 | 0.228 |
| Abs  = 525 nm | 0.114 | 0.002 | 0.002 | 0.003 | 0.002 | 0.001 | 0.202 |
| Abs  = 620 nm | 0.040 | 0.002 | 0.003 | 0.002 | 0.001 | 0.001 | 0.069 |
| TOC [mg · l-1] | 380 | 279 | 283 | 293 | 315 | 379 | 564 |
| TC [mg · l-1] | 383 | 279 | 283 | 293 | 315 | 379 | 570 |
| IC [mg · l-1] | 3 | 0 | 0 | 0 | 0 | 0 | 6 |

###### Second characterization of VRPW/NF

Flow rates in the second characterization and comparison among first, second and after washing characterization:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 6 | 19 |
| 6.9 | 22 |
| 9 | 29 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 6.9 | 23 | 22 | 4 |

###### Conclusions of VRPW/NF

The affinity observed is not very good but at increasing concentrations in the feed the fluydo-dynamic performances stay constant and a good recovery of flow rate is obtained in the second characterization.

The quality of the permeate is low, not acceptable for reuse tests. In particular organic content is high in the effluent because of the low removal. Colour is removed almost completely.

In this very case it must be noted that the combination UF +NF doe not give a better performance than the simple direct NF on the same effluent.

Comparison among flow rates measured in all the pilot scale trials:

Quality of the aver. permeate and percentage abatement:

|  | Feed | Permeate NF | Abatement % |
| --- | --- | --- | --- |
| pH | 9.4 | 9.8 | - |
| Conductivity [S·cm-1] | 664 | 262 | 65 |
| Turbidity [NTU] | - | - | - |
| Abs  = 426 nm | 0.129 | 0.005 | 98 |
| Abs  = 558 nm | 0.079 | 0.002 | 99 |
| Abs  = 460 nm | 0.026 | 0.001 | 99 |
| Abs  = 436 nm | 0.129 | 0.004 | 99 |
| Abs  = 525 nm | 0.114 | 0.002 | 99 |
| Abs  = 620 nm | 0.040 | 0.001 | 99 |
| TOC [mg · l-1] | 380 | 310 | 33 |
| TC [mg · l-1] | 383 | 310 | 38 |
| IC [mg · l-1] | 3 | 0 | 100 |

Overall removal efficiency of the train UF + NF, obtained combining the results of the single treatments:

|  | Abatement % UF | Abatement % NF | Overall Efficiency % |
| --- | --- | --- | --- |
| pH | - | - | - |
| Conductivity [S·cm-1] | 13% | 61% | 65% |
| Turbidity [NTU] | 67% | -20% | 60% |
| Abs  = 426 nm | 53% | 96% | 98% |
| Abs  = 558 nm | 64% | 97% | 99% |
| Abs  = 460 nm | 75% | 96% | 99% |
| Abs  = 436 nm | 52% | 97% | 99% |
| Abs  = 525 nm | 57% | 98% | 99% |
| Abs  = 620 nm | 74% | 98% | 99% |
| TOC [mg · l-1] | 18% | 18% | 33% |
| TC [mg · l-1] | 24% | 19% | 38% |
| IC [mg · l-1] | 93% | >99 | >99% |

##### Bench scale NF on SYRD effluent after UF

###### Characterization of SYRD/NF

Flow rate measurements at 6 bar pressure for three membranes at constant temperature (25 °C):

| P 6 bar | Membrane | T [°C] | QT [ l ·h-1·m-2 ] |
| --- | --- | --- | --- |
|  | DK | 25 | 46 |
|  | DL | 25 | 60 |
|  | HL | 25 | 60 |
|  | CK | 25 | 16 |

###### Complete recirculation test of SYRD/NF

Flow rate decrease passing to real effluent filtration at 6 bar pressure:

| Membrane | T (°C) | QT [ l · h-1· m-2 ] | Flow rate decrease [%] |
| --- | --- | --- | --- |
| DK | 37 | 22 | 65 |
| DL | 32 | 16 | 78 |
| HL | 40 | 18 | 80 |
| CK | 37 | <2 | 91 |

K=0.026

Permeates quality:

|  | Feed | DK | DL | HL |
| --- | --- | --- | --- | --- |
| pH | 9.5 | 9.6 | 9.5 | 9.5 |
| Conductivity [S·cm-1] | 35300 | 30100 | 32100 | 31300 |
| Turbidity [NTU] | 0.4 | 1 | 1 | 0.5 |
| Abs  = 426 nm | 2.070 | 0.022 | 0.022 | 0.051 |
| Abs  = 558 nm | 3.815 | 0.046 | 0.041 | 0.151 |
| Abs  = 660 nm | 0.027 | 0.009 | 0.008 | 0.007 |
| TOC [mg · l-1] | 451 | 81 | 121 | 125 |
| TC [mg · l-1] | 1090 | 321 | 471 | 450 |
| IC [mg · l-1] | 639 | 240 | 350 | 325 |

###### Choice of the membrane for the pilot scale

The best fluydodynamic performances among the membrane tested was obtained by membrane DL and also DK gave good results. On the contrary, CK has given so poor results was escluded from further investigation..

Membrane DK leaves in the permeates a residual organic content and conductivity significantly lower than DL. All this considered, both DK and DL were submitted to further investigation.

##### Pilot scale NF (membrane DK) on SYRD after UF

###### Pi. Sc. characterization of SYRD/NF (membrane DK)

Flow rates at different pressure values:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 6 | 12 |
| 6.9 | 13 |
| 9 | 17 |

###### Pi. Sc. complete recirculation test of SYRD/NF (membrane DK)

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 13 | 4 | 5 |
| 15 | 16 | 5 | 6 |
| 30 | 19 | 6 | 7 |
| 45 | 21 | 7 | 7 |
| 60 | 23 | 8 | 8 |

|  | Feed | permeate 60' |
| --- | --- | --- |
| pH | 9.5 | 9.6 |
| Conductivity [S·cm-1] | 37900 | 28300 |
| Turbidity [NTU] | 0.2 | 0.5 |
| Abs  = 436 nm | 2.234 | 0.007 |
| Abs  = 525 nm | 3.910 | 0.015 |
| Abs  = 620 nm | 0.019 | 0.003 |
| TOC [mg · l-1] | 482 | 69 |
| TC [mg · l-1] | 1140 | 315 |
| IC [mg · l-1] | 658 | 246 |

###### Concentration effect test of SYRD/NF (membrane DK)

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 20 | 8 | 9 |
| 20 | 19 | 7 | 8 |
| 40 | 21 | 7 | 8 |
| 60 | 21 | 7 | 8 |
| 80 | 24 | 8 | 8 |

|  | Feed | perm. 0% | perm. 20% | perm. 40% | perm. 60% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 9.5 | 9.6 | 9.6 | 9.6 | 9.6 | 9.5 | 9.5 |
| Conductivity [S·cm-1] | 37900 | 28600 | 28900 | 30000 | 31400 | 32700 | 37400 |
| Turbidity [NTU] | 0.2 | 0.4 | 0.4 | 0.3 | 0.3 | 0.8 | 0.3 |
| SST (mg l-1) | 38 | 41 | 35 | 33 | 41 | 41 | 31 |
| Abs  = 436 nm | 2.234 | 0.010 | 0.004 | 0.010 | 0.004 | 0.003 | 3.860 |
| Abs  = 525 nm | 3.910 | 0.018 | 0.011 | 0.016 | 0.010 | 0.015 | 4.215 |
| Abs  = 620 nm | 0.019 | 0.003 | 0.000 | 0.003 | 0.000 | 0.000 | 0.089 |
| TOC [mg · l-1] | 483 | 85 | 77 | 77 | 85 | 108 | 1055 |
| TC [mg · l-1] | 1140 | 353 | 351 | 401 | 475 | 602 | 2026 |
| IC [mg · l-1] | 658 | 268 | 274 | 324 | 390 | 494 | 971 |

♦ TOC in the feed

■ TOC in the permeate

###### Second characterization of SYRD/NF (membrane DK)

Flow rates in the second characterization and comparison among first, second and after washing characterization:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 6 | 12 |
| 6.9 | 13 |
| 9 | 18 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 6.9 | 14 | 14 | - |

###### Conclusions of SYRD/NF (membrane DK)

The affinity performed in this combination effluent/membrane is very low.

On the contrary, no loss is observed in the concentration effect test and no permanent material accumulation on the membrane occurs as observable in the second characteriazation flow rate value.

The permeate has a too high conductivity for reuse purposes due to high content in the feed, low removal and monovalent ions presence.

Comparison among flow rates measured in all the pilot scale trials:

Quality of the aver. permeate and percentage abatement:

|  | Feed | Permeate | Abatement % |
| --- | --- | --- | --- |
| pH | 9.5 | 9.6 | - |
| Conductivity [S·cm-1] | 37900 | 30320 | 20% |
| Turbidity [NTU] | 0.2 | 0.4 | -91% |
| SST (mg l-1) | 38 | 38.0 | 0% |
| Abs  = 436 nm | 2.234 | 0.006 | >99% |
| Abs  = 525 nm | 3.910 | 0.014 | >99% |
| Abs  = 620 nm | 0.019 | 0.001 | 94% |
| TOC [mg · l-1] | 483 | 86.5 | 82% |
| TC [mg · l-1] | 1140 | 436.4 | 62% |
| IC [mg · l-1] | 658 | 350.0 | 47% |

Overall removal efficiency of the train UF + NF, obtained combining the results of the single treatments:

|  | Abatement % UF | Abatement % NF | Overall Efficiency % |
| --- | --- | --- | --- |
| pH | - | - | - |
| Conductivity [S·cm-1] | 10% | 20% | 28% |
| Turbidity [NTU] | -143% | -91% | -364% |
| SST [mg · l-1] | 9% | 0% | 9% |
| Abs  = 426 nm | 27% | >99% | 99.8% |
| Abs  = 558 nm | 4% | >99% | >99% |
| Abs  = 660 nm | 1% | 94% | 94% |
| TOC [mg · l-1] | 43% | 82% | 90% |
| TC [mg · l-1] | 29% | 62% | 73% |
| IC [mg · l-1] | 16% | 47% | 55% |

##### Pilot scale NF (membrane DL) on SYRD after UF

###### Pi. Sc. characterization of SYRD/NF (membrane DL)

Flow rates at different pressure values:

| p [ bar ] | Q20 [ l · h-1] |
| --- | --- |
| 6 | 15 |
| 6.9 | 17 |
| 9 | 24 |

###### Pi. Sc. complete recirculation test of SYRD/NF (membrane DL)

Flow rate and quality of the permeates

| T [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 13 | 8 | 10 |
| 15 | 15 | 9 | 11 |
| 30 | 17 | 11 | 12 |
| 45 | 19 | 12 | 13 |
| 60 | 20 | 12 | 13 |

|  | Feed | permeate 60' |
| --- | --- | --- |
| pH | 9.5 | 9.5 |
| Conductivity [S·cm-1] | 37700 | 31400 |
| Turbidity [NTU] | 0.6 | 0.5 |
| Abs  = 436 nm | 2.136 | 0.003 |
| Abs  = 525 nm | 3.836 | 0.003 |
| Abs  = 620 nm | 0.022 | 0.001 |
| TOC [mg · l-1] | 472 | 90 |
| TC [mg · l-1] | 1116 | 367 |
| IC [mg · l-1] | 644 | 277 |

###### Concentration effect test of SYRD/NF (membrane DL)

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 19 | 11 | 12 |
| 20 | 20 | 12 | 14 |
| 40 | 21 | 12 | 13 |
| 60 | 22 | 12 | 13 |
| 80 | 23 | 12 | 12 |

|  | Feed | perm. 0% | perm. 20% | perm. 40% | perm. 60% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.4 | 9.5 |
| Conductivity [S·cm-1] | 37700 | 31400 | 31800 | 33000 | 33700 | 35500 | 41200 |
| Turbidity [NTU] | 0.6 | 1.4 | 0.3 | 0.3 | 0.6 | 0.5 | 0.4 |
| SST (mg l-1) | 50 | 43 | 47 | 55 | 43 | 67 | 40 |
| Abs  = 436 nm | 2.136 | 0.007 | 0.000 | 0.024 | 0.012 | 0.003 | 3.873 |
| Abs  = 525 nm | 3.836 | 0.013 | 0.000 | 0.017 | 0.010 | 0.007 | 4.174 |
| Abs  = 620 nm | 0.022 | 0.001 | 0.000 | 0.013 | 0.007 | 0.001 | 0.097 |
| TOC [mg · l-1] | 472 | 110 | 101 | 119 | 134 | 158 | 1229 |
| TC [mg · l-1] | 1116 | 402 | 401 | 473 | 564 | 733 | 2364 |
| IC [mg · l-1] | 644 | 292 | 301 | 354 | 430 | 575 | 1135 |

♦ TOC in the feed

■ TOC in the permeate

###### Second characterization of SYRD/NF (membrane DL)

Flow rates in the second characterization and comparison among first, second and after washing characterization:

| p [ bar ] | Q20 [ l · h-1] |
| --- | --- |
| 6 | 17 |
| 6.9 | 19 |
| 9 | 26 |

| P [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 6.9 | 19 | 21 | - |

###### Conclusions of SYRD/NF (membrane DL)

The affinity performed in this combination effluent/membrane is very low.

On the contrary, no loss is observed in the concentration effect test and no permanent material accumulation on the membrane occurs as observable in the second characteriazation flow rate value.

The permeate has a too high conductivity for reuse purposes due to high content in the feed, low removal and monovalent ions presence.

When compared with the DK nanofiltration, DL gives higher flow rates and lower removals.

Comparison among flow rates measured in all the pilot scale trials.

Quality of the aver. permeate and percentage abatement:

|  | Feed | Permeate | Abatement % |
| --- | --- | --- | --- |
| pH | 9.5 | 9.5 | - |
| Conductivity [S·cm-1] | 37700 | 33080 | 12% |
| Turbidity [NTU] | 0.6 | 0.6 | -13% |
| SST (mg l-1) | 50 | 51.2 | -2% |
| Abs  = 436 nm | 2.136 | 0.009 | >99% |
| Abs  = 525 nm | 3.836 | 0.009 | >99% |
| Abs  = 620 nm | 0.022 | 0.004 | 80% |
| TOC [mg · l-1] | 472 | 124.4 | 74% |
| TC [mg · l-1] | 1116 | 514.6 | 54% |
| IC [mg · l-1] | 644 | 390.2 | 39% |

Overall removal efficiency of the train UF + NF, obtained combining the results of the single treatments:

|  | Abatement % UF | Abatement % NF | Overall Efficiency % |
| --- | --- | --- | --- |
| pH | - | - | - |
| Conductivity [S·cm-1] | 10% | 12% | 21% |
| Turbidity [NTU] | -143% | -13% | -173% |
| SST [mg · l-1] | 9% | -2% | 7% |
| Abs  = 426 nm | 27% | >99% | >99% |
| Abs  = 558 nm | 4% | >99% | >99% |
| Abs  = 660 nm | 1% | 80% | 80% |
| TOC [mg · l-1] | 43% | 74% | 85% |
| TC [mg · l-1] | 29% | 54% | 67% |
| IC [mg · l-1] | 16% | 39% | 49% |

##### Pilot scale NF on CRD after UF

###### Pi. Sc. characterization of CRD/NF

Flow rates at different pressure values:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 6 | 20 |
| 6.9 | 23 |
| 9 | 29 |

###### Pi. Sc. complete recirculation test of CRD/NF

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 25 | 15 | 15 |
| 20 | 26 | 17 | 17 |
| 40 | 26 | 18 | 18 |
| 60 | 27 | 18 | 17 |

|  | Feed | permeate 0' | permeate 60' |
| --- | --- | --- | --- |
| pH | 9.9 | 9.2 | 9.3 |
| Conductivity [S·cm-1] | 17100 | 12882 | 13240 |
| Abs  = 426 nm | 0.430 | 0.006 | 0.004 |
| Abs  = 558 nm | 0.321 | 0.003 | 0.003 |
| Abs  = 660 nm | 0.133 | 0.003 | 0.004 |
| Abs  = 436 nm | 0.431 | 0.006 | 0.003 |
| Abs  = 525 nm | 0.322 | 0.004 | 0.003 |
| Abs  = 620 nm | 0.299 | 0.003 | 0.004 |
| TOC [mg · l-1] | 69 | 20 | 18 |
| TC [mg · l-1] | 322 | 76 | 75 |
| IC [mg · l-1] | 253 | 56 | 57 |

###### Concentration effect test of CRD/NF

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 27 | 18 | 17 |
| 30 | 27 | 17 | 16 |
| 60 | 28 | 17 | 16 |

|  | Feed | perm. 0% | perm. 30% | perm. 60% | Conc. |
| --- | --- | --- | --- | --- | --- |
| pH | 9.9 | 9.3 | 9.3 | 9.2 | 10.0 |
| Conductivity [S·cm-1] | 17100 | 13240 | 14040 | 15441 | 20207 |
| TOC [mg · l-1] | 69 | 18 | 19 | 22 | 126 |
| TC [mg · l-1] | 322 | 76 | 92 | 121 | 573 |
| IC [mg · l-1] | 253 | 57 | 73 | 99 | 447 |
| Abs  = 426 nm | 0.434 | 0.005 | 0.004 | 0.006 | 0.894 |
| Abs  = 558 nm | 0.318 | 0.004 | 0.001 | 0.002 | 0.637 |
| Abs  = 660 nm | 0.126 | 0.005 | 0.004 | 0.005 | 0.260 |
| Abs  = 436 nm | 0.432 | 0.004 | 0.004 | 0.007 | 0.890 |
| Abs  = 525 nm | 0.325 | 0.004 | 0.002 | 0.000 | 0.657 |
| Abs  = 620 nm | 0.305 | 0.005 | 0.002 | 0.005 | 0.623 |

###### Second characterization of CRD/NF

Flow rates in the second characterization and comparison among first, second and after washing characterization:

| p [ bar ] | Q25 [ l · h-1] |
| --- | --- |
| 6 | 19 |
| 6.9 | 23 |
| 9 | 30 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 6.9 | 23 | 23 | - |

###### Conclusions of CRD/NF

The affinity is not very high in this treatment and a little further decrease in flow rate is evidenced due to the concentration effect.

Good recovery of the initial maximum flow rate is performed in the second characterization.

The reuse is not possible due to high conductivity weakly removed while abatements of organic content and colour are high.

Comparison among flow rates measured in all the pilot scale trials:

Quality of the aver. permeate and percentage abatement:

|  | Feed | Permeate NF | Abatement % |
| --- | --- | --- | --- |
| pH | 9.9 | 9.3 |  |
| Conductivity [S·cm-1] | 17100 | 14240 | 17% |
| TOC [mg · l-1] | 69 | 20 | 71% |
| TC [mg · l-1] | 322 | 96 | 70% |
| IC [mg · l-1] | 253 | 76 | 70% |
| Abs  = 426 nm | 0.434 | 0.005 | 99% |
| Abs  = 558 nm | 0.318 | 0.002 | 99% |
| Abs  = 460 nm | 0.126 | 0.004 | 97% |
| Abs  = 436 nm | 0.432 | 0.005 | 99% |
| Abs  = 525 nm | 0.325 | 0.002 | 99% |
| Abs  = 620 nm | 0.305 | 0.004 | 99% |
| SST (mg l-1) |  |  |  |

Overall removal efficiency of the train UF + NF, obtained combining the results of the single treatments:

|  | Abatement % UF | Abatement % NF | Overall Efficiency % |
| --- | --- | --- | --- |
| pH |  |  |  |
| Conductivity [S·cm-1] | -2% | 17% | 15% |
| TOC [mg · l-1] | 45% | 71% | 84% |
| TC [mg · l-1] | 15% | 70% | 75% |
| IC [mg · l-1] | 1% | 70% | 70% |
| Abs  = 426 nm | 10% | 99% | 99% |
| Abs  = 558 nm | 11% | 99% | 99% |
| Abs  = 460 nm | 13% | 97% | 97% |
| Abs  = 436 nm | 10% | 99% | 99% |
| Abs  = 525 nm | 10% | 99% | 99% |
| Abs  = 620 nm | 11% | 99% | 99% |
| SST (mg l-1) | >99% |  | >99% |

#### Anaerobically pretreated CRD -direct NF results

The membrane choice was not performed on bench scale test results. The membrane DL has been chosen on the base of previous results on similar effluents.

##### Pilot scale NF on CRD effluent anaerobically pretreated

###### Pi. Sc. characterization of CRD/NF after anaer. treatm.

Flow rates at different pressure values:

| p [ bar ] | Q33 [ l · h-1] | Q35 [ l · h-1] | Q38 [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- | --- |
| 6 | 23 | 26 | 26 | 20 |
| 6.9 | 28 | 29 | 30 | 24 |
| 9 | 36 | 38 | 40 | 31 |

###### Pi. Sc. complete recirculation test of CRD/NF after anaer. treatm.

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 32 | 21 | 18 |
| 15 | 37 | 23 | 18 |
| 30 | 38 | 24 | 18 |
| 45 | 39 | 24 | 18 |
| 60 | 39 | 24 | 18 |

|  | Feed | permeate 0' | permeate 60' |
| --- | --- | --- | --- |
| pH | 8.8 | 8.3 | 8.8 |
| Conductivity [S·cm-1] | 18270 | 16040 | 16080 |
| Abs  = 426 nm | 0.199 | 0.012 | 0.002 |
| Abs  = 558 nm | 0.066 | 0.006 | 0.001 |
| Abs  = 660 nm | 0.033 | 0.004 | 0.001 |
| Abs  = 436 nm | 0.182 | 0.011 | 0.002 |
| Abs  = 525 nm | 0.086 | 0.007 | 0.002 |
| Abs  = 620 nm | 0.044 | 0.004 | 0.001 |
| TOC [mg · l-1] | 61 | 31 | 16 |
| TC [mg · l-1] | 308 | 161 | 151 |
| IC [mg · l-1] | 247 | 130 | 135 |

###### Concentration effect test of CRD/NF after anaer. treatm.

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 39 | 24 | 18 |
| 30 | 39 | 24 | 18 |
| 60 | 39 | 23 | 18 |

|  | Feed | perm. 0% | perm. 20% | perm. 60% | Conc. |
| --- | --- | --- | --- | --- | --- |
| pH | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 |
| Conductivity [S·cm-1] | 18270 | 16080 | 16580 | 17390 | 19880 |
| Abs  = 426 nm | 0.199 | 0.002 | 0.004 | 0.006 | 0.401 |
| Abs  = 558 nm | 0.066 | 0.001 | 0.002 | 0.001 | 0.134 |
| Abs  = 660 nm | 0.033 | 0.001 | 0.003 | 0.001 | 0.071 |
| Abs  = 660 nm | 0.182 | 0.002 | 0.003 | 0.006 | 0.366 |
| Abs  = 660 nm | 0.086 | 0.002 | 0.001 | 0.002 | 0.172 |
| Abs  = 660 nm | 0.044 | 0.001 | 0.003 | 0.001 | 0.091 |
| TOC [mg · l-1] | 61 | 16 | 13 | 15 | 133 |
| TC [mg · l-1] | 308 | 151 | 162 | 195 | 452 |
| IC [mg · l-1] | 247 | 135 | 149 | 180 | 319 |
| SST[mg l-1] | 28 | - | - | - | 26 |

###### Second characterization of CRD/NF after anaer. treatm.

Flow rates in the second characterization and comparison between first and second characterization:

| p [ bar ] | Q33 [ l · h-1] | Q35 [ l · h-1] | Q38 [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- | --- |
| 6 | 23 | 25 | 26 | 20 |
| 6.9 | 27 | 29 | 30 | 23 |
| 9 | 36 | 36 | 38 | 30 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 6.9 | 24 | 23 | 4 |

###### Conclusions of CRD/NF after anaer. treatm.

The affinity is not very high while the flow rate stays almost constant during the concentration effect test.

Good recovery of the initial maximum flow rate is performed in the second characterization.

The reuse is not possible due to high conductivity weakly removed while abatements of organic content and colour are very high as for the ffluent without anaerobic pre-treatment.

Comparison among flow rates measured in all the pilot scale trials.

Quality of the aver. permeate and percentage abatement

|  | Feed | Permeate | Abatement % |
| --- | --- | --- | --- |
| pH | 8.8 | 8.8 | - |
| Conductivity [S·cm-1] | 18270 | 16683 | 9% |
| Abs  = 426 nm | 61 | 15 | 76% |
| Abs  = 558 nm | 308 | 169 | 45% |
| Abs  = 660 nm | 247 | 155 | 37% |
| Abs  = 436 nm | 0.199 | 0.004 | 98% |
| Abs  = 525 nm | 0.066 | 0.001 | 98% |
| Abs  = 620 nm | 0.033 | 0.002 | 95% |
| TOC [mg] | 0.182 | 0.004 | 98% |
| TC [mg · l-1] | 0.086 | 0.002 | 98% |
| IC [mg · l-1] | 0.044 | 0.002 | 96% |
| SST [mg· l-1] | 28 | - | >99 |

#### Anaerobically pretreated CRD -UF results

UF membrane choice was performed on the base of previous experimental results. Membrane labelled MW, produced by Osmonics Inc. was selected. Investigation was carried out on pilot scale.

##### Pilot scale UF on CRD effluent anaerobically pretreated

###### Pi. Sc. characterization of CRD/UF anaerobically pretreated

Flow rates at different pressure and temperature values:

| p [ bar ] | Q28 [ l · h-1] | Q30 [ l · h-1] | Q33 [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- | --- |
| 1.4 | 39 | 39 | 40 | 38 |
| 1.9 | 49 | 49 | 50 | 47 |
| 2.3 | 54 | 54 | 58 | 53 |
| 2.8 | 64 | 64 | 68 | 62 |

###### Pi. Sc. complete recirculation test of CRD/UF anaerobically pretreated

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 21 | 39 | 40 |
| 15 | 22 | 34 | 32 |
| 30 | 23 | 31 | 31 |
| 45 | 23 | 30 | 30 |
| 60 | 23 | 30 | 30 |

|  | Feed | permeate 0' | permeate 60' |
| --- | --- | --- | --- |
| pH | 8.5 | 8.2 | 8.4 |
| Conductivity [S·cm-1] | 20300 | 20200 | 20200 |
| Abs  = 426 nm | 0.194 | 0.146 | 0.117 |
| Abs  = 558 nm | 0.067 | 0.048 | 0.039 |
| Abs  = 660 nm | 0.037 | 0.026 | 0.021 |
| Abs  = 436 nm | 0.177 | 0.134 | 0.107 |
| Abs  = 525 nm | 0.085 | 0.060 | 0.050 |
| Abs  = 620 nm | 0.046 | 0.033 | 0.026 |
| TOC [mg · l-1] | 48 | 36 | 29 |
| TC [mg · l-1] | 338 | 335 | 325 |
| IC [mg · l-1] | 290 | 299 | 296 |

###### Concentration effect test of CRD/UF anaerobically pretreated

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 23 | 30 | 30 |
| 40 | 23 | 30 | 30 |
| 80 | 23 | 28 | 28 |

|  | Feed | perm. 0% | perm. 40% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- |
| pH | 8.5 | 8.4 | 8.5 | 8.5 | 8.5 |
| Conductivity [S·cm-1] | 20300 | 20200 | 20200 | 20100 | 20200 |
| TOC [mg · l-1] | 48 | 29 | 38 | 39 | 84 |
| TC [mg · l-1] | 338 | 325 | 331 | 332 | 376 |
| IC [mg · l-1] | 290 | 296 | 293 | 293 | 292 |
| Abs  = 426 nm | 0.194 | 0.117 | 0.133 | 0.156 | 0.311 |
| Abs  = 558 nm | 0.067 | 0.039 | 0.043 | 0.051 | 0.114 |
| Abs  = 660 nm | 0.037 | 0.021 | 0.023 | 0.026 | 0.065 |
| Abs  = 436 nm | 0.177 | 0.107 | 0.121 | 0.142 | 0.286 |
| Abs  = 525 nm | 0.085 | 0.05 | 0.055 | 0.065 | 0.143 |
| Abs  = 620 nm | 0.046 | 0.026 | 0.03 | 0.034 | 0.081 |
| SST [mg · l-1] | 33.3 | - | - | - | 43.3 |

###### Second characterization of CRD/UF anaerobically pretreated

Flow rates in the second characterization and comparison between first and second characterization:

| p [ bar ] | Q28 [ l · h-1] | Q30 [ l · h-1] | Q33 [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- | --- |
| 1.4 | 39 | 39 | 40 | 38 |
| 1.9 | 48 | 49 | 49 | 47 |
| 2.3 | 52 | 55 | 55 | 52 |
| 2.8 | 62 | 63 | 65 | 12 |

| P [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 2.1 | 50 | 49 | 2 |

###### Conclusions of CRD/UF anaerobically pretreated

The affinity between membrane and pre-treated effluent is poor, showing a decrease of affinity when compared with the raw effluent.

During the concentration effected test the flow rates do not decrease; an almost complete recovery of flow rate occurs during the second characterization.

The removals are very poor.

Comparison among flow rates measured in all the pilot scale trials:

Comparison among flow rates measured in all the pilot scale trials:

|  | Feed | Permeate UF | Abatement % |
| --- | --- | --- | --- |
| PH | 8.5 | 8.5 | - |
| Conductivity [S·cm-1] | 20300 | 20167 | 1% |
| TOC [mg · l-1] | 48 | 35 | 26% |
| TC [mg · l-1] | 338 | 329 | 3% |
| IC [mg · l-1] | 290 | 294 | -1% |
| Abs  = 426 nm | 0.194 | 0.135 | 30% |
| Abs  = 558 nm | 0.067 | 0.044 | 34% |
| Abs  = 460 nm | 0.037 | 0.023 | 37% |
| Abs  = 436 nm | 0.177 | 0.123 | 30% |
| Abs  = 525 nm | 0.085 | 0.057 | 33% |
| Abs  = 620 nm | 0.046 | 0.030 | 35% |
| SST [m l-1] | 33.3 | - | >99% |

The permeate effluent from ultrafiltration is submitted to nanofiltration as described in § 4.7.2.6.1.

#### Anaerobically pretreated CRD -UF+NF results

The membrane choice was not performed on bench scale test results. The membrane DL has been chosen on the base of previous results on similar effluents.

##### Pilot scale NF on anaerobically pretreated CRD effluent after UF

###### Pi. Sc. characterization of anaerobically pretreated CRD/NF after UF

Flow rates at different pressure values:

| p [ bar ] | Q33 [ l · h-1] | Q35 [ l · h-1] | Q38 [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- | --- |
| 6 | 23 | 25 | 26 | 20 |
| 6.9 | 27 | 29 | 30 | 23 |
| 9 | 36 | 36 | 40 | 30 |

###### Pi. Sc. complete recirculation test of anaerobically pretreated CRD/NF after UF

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 32 | 20 | 17 |
| 15 | 36 | 22 | 18 |
| 30 | 37 | 22 | 17 |
| 45 | 37 | 22 | 17 |
| 60 | 37 | 23 | 18 |

|  | Feed | permeate 0' | permeate 60' |
| --- | --- | --- | --- |
| pH | 9.0 | 8.9 | 9.0 |
| Conductivity [S·cm-1] | 20058 | 16977 | 17442 |
| Abs  = 426 nm | 0.151 | 0.013 | 0.008 |
| Abs  = 558 nm | 0.052 | 0.003 | 0.002 |
| Abs  = 660 nm | 0.029 | 0.006 | 0.003 |
| Abs  = 436 nm | 0.144 | 0.010 | 0.007 |
| Abs  = 525 nm | 0.063 | 0.004 | 0.002 |
| Abs  = 620 nm | 0.032 | 0.006 | 0.003 |
| TOC [mg · l-1] | 41 | 1 | 14 |
| TC [mg · l-1] | 299 | 136 | 149 |
| IC [mg · l-1] | 258 | 135 | 135 |

###### Concentration effect test of anaerobically pretreated CRD/NF after UF

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 37 | 23 | 18 |
| 30 | 38 | 23 | 18 |
| 60 | 38 | 23 | 18 |

|  | Feed | perm. 0% | perm. 30% | perm. 60% | Conc. |
| --- | --- | --- | --- | --- | --- |
| pH | 9.0 | 9.0 | 9.0 | 9.0 | 9.0 |
| Conductivity [S·cm-1] | 20058 | 17442 | 18023 | 19105 | 22198 |
| TOC [mg · l-1] | 41 | 14 | 15 | 3 | 105 |
| TC [mg · l-1] | 299 | 149 | 162 | 197 | 460 |
| IC [mg · l-1] | 258 | 135 | 147 | 193 | 356 |
| Abs  = 426 nm | 0.150 | 0.008 | 0.007 | 0.013 | 0.312 |
| Abs  = 558 nm | 0.049 | 0.002 | 0.000 | 0.005 | 0.097 |
| Abs  = 660 nm | 0.027 | 0.003 | 0.001 | 0.005 | 0.051 |
| Abs  = 436 nm | 0.136 | 0.007 | 0.006 | 0.012 | 0.281 |
| Abs  = 525 nm | 0.062 | 0.002 | 0.001 | 0.005 | 0.123 |
| Abs  = 620 nm | 0.034 | 0.003 | 0.000 | 0.006 | 0.066 |
| SST [mg · l-1] | 25 | - | - | - | 26 |

###### Second characterization of anaerobically pretreated CRD/NF after UF

Flow rates in the second characterization and comparison among first, second and after washing characterization:

| p [ bar ] | Q33 [ l · h-1] | Q35 [ l · h-1] | Q38 [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- | --- |
| 6 | 23 | 26 | 26 | 20 |
| 6.9 | 28 | 29 | 30 | 24 |
| 9 | 36 | 38 | 40 | 31 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 6.9 | 23 | 24 | - |

###### Conclusions of anaerobically pretreated CRD/NF after UF

Quite good affinity is observed comparind the first characterization flow rate with the real effluent filtration. The concentration effect shows no loss in flow rate and a good recovery of the initial maximum value is obtained during the second characterization.

The quality of the permeate and the removals are not improved with respect to the direct NF, the conductivity being the main obstacle to possible reuse.

Comparison among flow rates measured in all the pilot scale trials:

Quality of the aver. permeate and percentage abatement:

|  | Feed | Permeate NF | Abatement % |
| --- | --- | --- | --- |
| pH | 9.0 | 9.0 | - |
| Conductivity [S·cm-1] | 20058 | 18189.9 | 9% |
| TOC [mg · l-1] | 41 | 10.9 | 73% |
| TC [mg · l-1] | 299 | 169.0 | 43% |
| IC [mg · l-1] | 258 | 158.1 | 39% |
| Abs  = 426 nm | 0.150 | 0.009 | 94% |
| Abs  = 558 nm | 0.049 | 0.002 | 95% |
| Abs  = 460 nm | 0.027 | 0.003 | 88% |
| Abs  = 436 nm | 0.136 | 0.008 | 94% |
| Abs  = 525 nm | 0.062 | 0.003 | 96% |
| Abs  = 620 nm | 0.034 | 0.003 | 91% |

Overall removal efficiency of the train UF + NF, obtained combining the results of the single treatments:

|  | Abatement % UF | Abatement % NF | Overall Efficiency % |
| --- | --- | --- | --- |
| pH | - | - | - |
| Conductivity [S·cm-1] | 1% | 9% | 10% |
| TOC [mg · l-1] | 26% | 73% | 80% |
| TC [mg · l-1] | 3% | 43% | 45% |
| IC [mg · l-1] | -1% | 39% | 38% |
| Abs  = 426 nm | 30% | 94% | 96% |
| Abs  = 558 nm | 34% | 95% | 97% |
| Abs  = 460 nm | 37% | 88% | 93% |
| Abs  = 436 nm | 30% | 94% | 96% |
| Abs  = 525 nm | 33% | 96% | 97% |
| Abs  = 620 nm | 35% | 91% | 94% |
| SST (mg l-1) | >99%! | - | >99% |

### Assessment of changes in aerobic biodegradability using respirometry

For the introduction on this assessment see chapter 4.6.3. The aerobic biodegradability of the reactive dyeing wastewater, the anaerobically treated sample and the membrane concentrates and permeate are shown in Figure 66. For clarity of the figure, only the trendlines have been made visible.

Figure 66 - Changes in aerobic biodegradability measured using respirometry. Tested amount was 50 ml for all samples.

The original wastewater gives already a large response, indicating that the reactive dyeing wastewater has an aerobically biodegradable fraction. Anaerobic treatment improves the biodegradability, probably because aerobically on-biodegradable azo dyes were converted to aerobically biodegradable aromatic amines. This is just an assumption, as the chemical structures of the dyes present in the reactive dyeing wastewater have not been released. The membrane-filtered samples gave only a small response.

### Tech./econ. feasibility of anaerobic treatment

Although the reactor set-up used in the experiments was not optimised, it can serve as a base for the full-size reactor calculation. The experimental reactor configuration for acid dyeing wastewater has been given in Table 9. Using this same configuration with the amount of wastewater as is available in the factory a full-scale reactor was calculated. Data on the discharged amounts of wastewater were taken from the PIDACS document of the respective company. See Table 19 for the results.

Table 19, Scale up to full size of the experimental reactor treating Reactive dyeing wastewater. Two volumes were considered: the total wastewater volume coming from the same type of process as the wastewater tested in the reactor (reactive dyeing) and the wastewater volume of all dyeing processes performed in the factory

|  |  |  | Reactive dyeing wastewater | All dyeing wastewater |
| --- | --- | --- | --- | --- |
| Reactor design | yearly supply of ww (Q) | m3/year | 156213 | 274058 |
|  | hourly supply of ww (Q) | m3/hour | 18 | 31 |
|  | Hydraulic residence time (HRT) | h | 8.8 | 8.8 |
|  | Chosen reactor height (H) | H | 5 | 5 |
|  | Reactor volume (Vr) | = Q * HRT | 156.2 | 274.1 |
|  | Reactor area (A) | = Vr / H | 31.2 | 54.8 |
|  | Upflow velocity (v) | = Q / A | 0.6 | 0.6 |
| Construction costs | Low estimation of construction costs in € | = 200 * m3 | € 54675 | € 95920 |
|  | High estimation of construction costs in € | = 350 * m3 | € 78107 | € 137029 |
| Cost calculation for high price / m3 reactor volume, based on 10 years of duration | Interest - average per year (1) | 4% / year | € 3762 | € 6844 |
|  | Maintenance (2) | 3% / year | € 2343 | € 4111 |
|  | Operation - manpower 0.25 person (3) | 12*1000 | € 12000 (4) | € 12000 |
|  | Construction costs per year (4) | Costs/10 | € 7812 | € 13703 |
|  | Total cost per year | sum 1 to 4 | € 25917 | € 36658 |
|  | Total costs per m3 wastewater |  | € 0.17 | € 0.13 |

To calculate the operational costs, it was assumed that manpower would consist of one person on a 25% job. Employing an operator costs a company around € 4000,- per month, so the total amount for one year of operation would be 12 x € 1000,-.

### Tech./econ. feasibility of membrane treatment

In the following paragraph the technical – economical aspects related to the treatment and reuse of the effluents are presented, independently from the considerations on permeates reusability exposed in the previous paragraphs.

In the table below, for all the treatments tested on reactive dyeing and printing effluents, the values of three flow indexes are reported as resulted from the experimental runs. I1 describes the affinity membrane – effluent, I2 the reduction of permeate flow at increased feed concentration and I3 is an estimation of the hours of operation before washing is required.

Refer to § 3.2.3.4. to have a description of how the indexes are calculated and their influence on the economical evaluations.

In the following tables and graphs all the details of the economical evaluations are reported for each effluent and treatment tested, in § 3.2.3.4. the method applied is explained with the assumptions behind it.

It can be noted that:

- The treatment trains tested UF, NF and UF+NF have shown a potentially high feasibility in terms of costs.

- The direct NF of anaerobically pretreated cotton reactive dyeing (CRDa)effluent seems to be economically feasible. Small advantages resulted in UF+NF treatment of anaerobically pretreated effluent.

#### Cost estimation UF/CRD

#### Cost estimation UF/SYRD

#### Cost estimation UF/VRPW

#### Cost estimation UF +NF/CRD

#### Cost estimation UF+NF/SYRD

#### Cost estimation UF+NF/VRPW

#### Cost estimation NF/VRPW

#### Cost estimation UF/CRDa

#### Cost estimation UF+NF/CRDa

#### Cost estimation NF/CRDa

### Reuse tests results (dyeing rinsing and printing)

#### Reuse of reactive dyeing permeate for reactive dyeing of cotton

The permeate of reactive dyeing has been reused for reactive dyeing of cotton both in a light and a dark colour shade.

##### Colour differences

|  | % permeate | delta E (CMC2:1) |
| --- | --- | --- |
| reference | 0% |  |
| light | 100% | 1,72 |
| light | 75% | 1,70 |
| reference | 0% |  |
| dark | 100% | 0,53 |
| dark | 75% | 0,36 |

For each colour shade the fabric, dyed with 100% fresh process water, has been taken as the reference to calculate the difference in colour. For the light colour shade the difference in colour is significant and also visually very obvious. For the dark colour shade the colour differences are below 0.8, which means that no significant changes in colour shade can be measured. Also visually no differences were observed.

##### Colour fastness to rubbing

|  | light |  |  | dark |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| % permeate | 0% | 100% | 75% | 0% | 100% | 75% |
| change of shade |  |  |  |  |  |  |
| dry | 4-5 | 4-5 | 4-5 | 4 | 4 | 4 |
| wet | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 |
| staining |  |  |  |  |  |  |
| dry | 5 | 5 | 5 | 4-5 | 4-5 | 4-5 |
| wet | 4-5 | 4-5 | 4-5 | 3-4 | 3-4 | 3-4 |

All values are good to very good and no differences higher than 0.5 unit are noticed.

##### Colour fastness to washing

|  | light |  |  | dark |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| %permeate | 0% | 100% | 75% | 0% | 100% | 75% |
| change of shade | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 |
| staining |  |  |  |  |  |  |
| cotton | 4-5 | 4-5 | 4 | 4-5 | 4 | 4 |
| viscose | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 | 4-5 |

All values are good to very good and no differences higher than 0.5 unit are noticed.

##### Conclusions: reuse of permeate for reactive dyeing of cotton

The reuse of reactive permeate for reactive dyeing of cotton does not have a negative influence on the fastness properties of the dyed fabric.

The dyed fabrics however show a significant difference in colour for the light colour shade. The reason for this is the higher conductivity of the permeate, i.e. 12100 µS/cm instead of 811 µS/cm in the fresh process water. The salt regulates the speed of the dyeing and the depth of the colour. The darker the colour shade the more salt is used. For the light colour shade the relative difference in salt concentration between fresh process water and reused permeate is much higher than for the dark colour shade. Moreover for dyeing dark colours with reactive dyestuff an overdosis of salt is dosed. As a consequence the extra amount of salt present in the permeate does not have a big impact.

Another important difference between both waterqualities is the pH: 7.8 (process water) versus 9.3 (permeate).

Therefore as a conclusion it should be stated that reuse of reactive permeate for reactive dyeing of cotton is not possible without adjusting the pH and the salt concentration. Altering the pH is not a big problem but decreasing the salt concentration implies the put in of extra treatment techniques, for instance reverse osmosis. Another way of dealing with the high salt concentration, is dosing less salt in the dyeing bath. A difficulty is the need for an on line measurement of sodium ions. An on line measurement of conductivity is not enough since there exist no straight correlation between conductivity and concentration of sodium ions.

#### Reuse of reactive dyeing permeate for direct dyeing of cotton

The permeate of reactive dyeing has been reused for direct dyeing of cotton both in a medium and a dark colour shade.

##### Colour differences

|  | % permeate | delta E (CMC2:1) |
| --- | --- | --- |
| reference | 0% |  |
| medium | 100% | 1,09 |
| medium | 75% | 0,98 |
| reference | 0% |  |
| dark | 100% | 1,67 |
| dark | 75% | 1,32 |

For each colour shade the fabric, dyed with 100% fresh process water, has been taken as the reference to calculate the difference in colour. For both the light and the dark colour shade the differences in colour are significant and also visually very obvious.

##### Colour fastness to rubbing

|  | medium |  |  | dark |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| % permeate | 0% | 100% | 75% | 0% | 100% | 75% |
| change of shade |  |  |  |  |  |  |
| dry | 4-5 | 4-5 | 4-5 | 4 | 4 | 4 |
| wet | 4 | 4 | 4 | 4 | 4 | 4 |
| staining |  |  |  |  |  |  |
| dry | 5 | 5 | 5 | 4-5 | 4-5 | 4-5 |
| wet | 4 | 3-4 | 3-4 | 3 | 2-3 | 2-3 |

The differences between the reference and the treatments with reused permeate are always lower than 0.5.

##### Colour fastness to washing

|  | medium |  |  | dark |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| %permeate | 0% | 100% | 75% | 0% | 100% | 75% |
| change of shade | 4 | 4-5 | 4 | 4 | 3-4 | 3-4 |
| staining |  |  |  |  |  |  |
| wool | 4 | 4-5 | 4 | 3-4 | 3-4 | 3-4 |
| cotton | 4-5 | 4 | 4 | 4 | 3-4 | 3 |

The differences between the reference and the treatments with reused permeate are always lower than 0.5.

##### Conclusions: reuse of permeate for direct dyeing of cotton

The reuse of reactive permeate for direct dyeing of cotton does not have a negative influence on the fastness properties of the dyed fabric.

The dyed fabrics however show a significant difference in colour for both the medium and the dark colour shade. The reason for this is the higher conductivity of the permeate, i.e. 12100 µS/cm instead of 811 µS/cm in the fresh process water. The salt regulates the speed of the dyeing and the depth of the colour. The darker the colour shade the more salt is used. For direct dyeing less salt is used than for reactive dyeing so the relative difference in salt concentration in the dyebath, prepared with fresh process water or with reused permeate, is much higher than for reactive dyeing. As a consequence the extra amount of salt present in the permeate has a bigger impact.

Another important difference between both waterqualities is the pH: 7.8 (process water) versus 9.3 (permeate).

Therefore as a conclusion it should be stated that reuse of reactive permeate for direct dyeing of cotton is not possible without adjusting the pH and the salt concentration. Altering the pH is not a big problem but decreasing the salt concentration implies the put in of extra treatment techniques, for instance reverse osmosis. Another way of dealing with the high salt concentration, is dosing less salt in the dyeing bath. A difficulty is the need for an on line measurement of sodium ions. An on line measurement of conductivity is not enough since there exist no straight correlation between conductivity and concentration of sodium ions.

## Viscose direct dyeing rinsing

In the present chapter, discussion and results of the experimental activities carried out on nanofiltration of the viscose direct dyeing rinsing (VDDR) effluent is reported.

### Membrane treatment results

#### Direct NF results

Direct nanofiltration has been applied on VDDR effluent. The results of the tests carried out according to the methods described above, on bench scale and on pilot scale are here reported.

##### Bench scale VDDR/NF

###### Characterization of VDDR/NF

Flow rate measurements at 6 bar pressure for three membranes at varying temperature and reported at 25 °C:

| P 6 bar | Membrane | T [°C] | QT [ l ·h-1·m-2 ] | k | Q25 [ l ·h-1·m-2 ] |
| --- | --- | --- | --- | --- | --- |
|  | DK | 37 | 65 | 0.028 | 46 |
|  | DL | 35 | 81 | 0.023 | 65 |
|  | HL | 35 | 87 | 0.027 | 66 |

###### Complete recirculation test of VDDR/NF

Flow rate decrease passing to real effluent filtration:

| P 6 bar | Membrane | Q25 [ l · h-1· m-2 ] | Flow rate decrease [%] |
| --- | --- | --- | --- |
|  | DK | 40 | 12 |
|  | DL | 61 | 5 |
|  | HL | 56 | 16 |

Permeates quality:

|  | Feed | DK | DL | HL |
| --- | --- | --- | --- | --- |
| pH | 7.7 | 7.4 | 7.8 | 7.6 |
| Conductivity [S·cm-1] | 697 | 401 | 537 | 433 |
| Turbidity [NTU] | 0.75 | 0.30 | 0.65 | 0.30 |
| Abs  = 426 nm | 0.033 | 0.007 | 0.001 | 0.009 |
| Abs  = 558 nm | 0.032 | 0.008 | 0.001 | 0.006 |
| Abs  = 660 nm | 0.015 | 0.003 | 0.002 | 0.005 |
| TOC [mg · l-1] | 0 | 1 | 2 | 1 |
| TC [mg · l-1] | 10 | 3 | 8 | 5 |
| IC [mg · l-1] | 10 | 2 | 6 | 4 |

###### Choice of the membrane for the pilot scale

The decrease of flow rate passing from deionised water to real effluent filtration is low for all the three membranes. DL has the best fluid-dynamic affinity.

Membrane DK have the best removal efficiency on conductivity. The other parameters have very low values in the feed, therefore no evaluation is possible.

DK is chosen for further investigation.

##### Pilot scale test of VDDR/NF

###### Pi. Sc. characterization of VDDR/NF

Flow rates at different pressure values:

| p [ bar ] | Q30 [ l · h-1] | Q33 [ l · h-1] | Q35 [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- | --- |
| 6 | 18 | 19 | 20 | 14 |
| 6.9 | 21 | 22 | 23 | 16 |
| 9 | 28 | 29 | 30 | 21 |

###### Pi. Sc. complete recirculation test of VDDR/NF

Flow rate and quality of the permeates

| t [ min ] | T [ °C ] | QT [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 0 | 34 | 18 | 14 |
| 15 | 35 | 20 | 15 |
| 30 | 36 | 20 | 15 |
| 45 | 37 | 20 | 14 |
| 60 | 38 | 20 | 14 |

|  | Feed | permeate 0' | permeate 60' |
| --- | --- | --- | --- |
| pH | 7.5 | 7.5 | 7.5 |
| Conductivity [S·cm-1] | 745 | 452 | 461 |
| Turbidity [NTU] | 0.72 | 0.17 | 0.18 |
| Abs  = 426 nm | 0.033 | 0.003 | 0.004 |
| Abs  = 558 nm | 0.032 | 0.001 | 0.002 |
| Abs  = 660 nm | 0.015 | 0.003 | 0.004 |
| TOC [mg · l-1] | 1 | 2 | 1 |
| TC [mg · l-1] | 11 | 7 | 5 |
| IC [mg · l-1] | 10 | 5 | 4 |

###### Concentration effect test of VDDR/NF

Flow rates and permeates quality at different level of feed concentration:

| Conc. [ % ] | T [ °C ] | QT [ l · h-1 ] | Q25 [ l · h-1 ] |
| --- | --- | --- | --- |
| 0 | 36 | 20 | 14 |
| 20 | 38 | 20 | 14 |
| 40 | 39 | 20 | 13 |
| 60 | 40 | 21 | 14 |
| 80 | 41 | 21 | 13 |

|  | Feed | perm. 0% | perm. 20% | perm. 40% | perm. 60% | perm. 80% | Conc. |
| --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 7.5 | 7.5 | 7.5 | 7.5 | 7.7 | 7.8 | 8.0 |
| Conductivity [S·cm-1] | 745 | 454 | 492 | 556 | 663 | 879 | 1384 |
| Turbidity [NTU] | 0.72 | 0.22 | 0.16 | 0.12 | 0.22 | 0.34 | 1.90 |
| Abs  = 426 nm | 0.033 | 0.008 | 0.010 | 0.003 | 0.002 | 0.009 | 0.086 |
| Abs  = 558 nm | 0.032 | 0.003 | 0.003 | 0.003 | 0.002 | 0.011 | 0.049 |
| Abs  = 660 nm | 0.015 | 0.004 | 0.008 | 0.006 | 0.003 | 0.009 | 0.054 |
| TOC [mg · l-1] | 1 | 1 | 1 | 1 | 1 | 0 | 3 |
| TC [mg · l-1] | 11 | 5 | 6 | 7 | 8 | 12 | 29 |
| IC [mg · l-1] | 10 | 4 | 5 | 6 | 7 | 12 | 26 |

♦ TOC in the feed

■ TOC in the permeate

###### Second characterization of VDDR/NF

Flow rates in the second characterization and comparison between first and second characterization:

| p [ bar ] | Q35 [ l · h-1] | Q38 [ l · h-1] | Q25 [ l · h-1] |
| --- | --- | --- | --- |
| 6 | 17 | 18 | 13 |
| 6.9 | 20 | 20 | 14 |
| 9 | 26 | 28 | 19 |

| p [bar] | Q25 charact. [ l · h-1] | Q25 II charact. [ l · h-1] | Loss % |
| --- | --- | --- | --- |
| 6 | 14 | 13 | 7 |
| 6.9 | 16 | 14 | 13 |
| 9 | 21 | 19 | 10 |

###### Conclusions of VDDR/NF

During the nanofiltration with real effluent on pilot scale, a slight flow rate decrease occurred showing a quite good affinity.

The concentration effect test showed that the flow rate stays constant at the beginning, than a light decrease occurs.

During the second characterization a certain loss of flow rate occurs, showing some clogging on the membrane surface and need for chemical washing.

The quality of the permeate is acceptable for reuse tests (see §4.8.4.) even if some abatement percentile are low (organic content –too low in the feed, colour, conductivity –due to the presence of mono-valent salts).

Comparison among flow rates measured in all the pilot scale trials:

Quality of the aver. permeate and percentage abatement:

|  | Feed | Permeate | Abatement % |
| --- | --- | --- | --- |
| pH | 7.5 | 7.6 | - |
| Conductivity [S·cm-1] | 745 | 609 | 18 |
| Turbidity [NTU] | 0.7 | 0.2 | 71 |
| Abs  = 426 nm | 0.033 | 0.002 | 94 |
| Abs  = 558 nm | 0.032 | 0.001 | 97 |
| Abs  = 660 nm | 0.015 | 0.002 | 87 |
| TOC [mg · l-1] | 1 | 1 | 0 |
| TC [mg · l-1] | 11 | 8 | 32 |
| IC [mg · l-1] | 10 | 7 | 35 |

### Technical - economical feasibility

In the following paragraph the technical – economical aspects related to the treatment and reuse of the effluents are presented, independently from the considerations on permeates reusability exposed in the previous paragraphs.

In the table below, for all the treatments tested on direct dyeing effluent, the values of three flow indexes are reported as resulted from the experimental runs. I1 describes the affinity membrane – effluent, I2 the reduction of permeate flow at increased feed concentration and I3 is an estimation of the hours of operation before washing is required.

Refer to § 3.2.3.4. to have a description of how the indexes are calculated and their influence on the economical evaluations.

In the following tables and graphs all the details of the economical evaluations are reported for each effluent and treatment tested, in § 3.2.3.4. the method applied is explained with the assumptions behind it.

It can be noted that:

- The NF treatment trains tested have shown a potentially high feasibility in terms of costs.

#### Cost estimation NF/VDDR

### Reuse tests results (dyeing rinsing and printing)

#### Reuse of direct dyeing permeate for scouring of viscose

##### Scouring efficiency

The verification of the degree of scouring was checked by means of the determination of the degree of whiteness.

| TREATMENT | DEGREE OF WHITE | x | y | Y |
| --- | --- | --- | --- | --- |
| REFERENCE | 66.2 | 0.3157 | 0.333 | 71.1 |
| REUSE | 64.9 | 0.316 | 0.3334 | 70.7 |

The higher the value, the more white is the sample. The measured degree of whiteness is acceptable and the differences are less than 5 units.

#### Reuse of direct dyeing permeate for direct and reactive dyeing of viscose

##### Colour differences

DYE WITH DIRECT DYES (SOLIAMINA – ALPHA COLOR)

| Formula: CMC 2.0:1.0 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Substratum: 100% VISCOSE |  |  |  |  |  |
| Reference: COL. GREY- DYE WITH INDUSTRIAL WATER |  |  |  |  |  |
| Sample: COL. GREY – DYE WITH TREATED WATER |  |  |  |  |  |
|  | delE | delL | delC | delH | The sample is |
| D65/10 | 0.463 | 0.313 | -0.253 | 0.229 | + clear + dirty + blue |
| A/10 | 0.492 | 0.304 | -0.335 | 0.191 | + clear + dirty + blue |
| F11/10 | 0.492 | 0.303 | -0.314 | 0.228 | + clear + dirty + blue |

| Formula: CMC 2.0:1.0 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Substratum: 100% VISCOSE |  |  |  |  |  |
| Reference: COL. BLUE SEA – DYE WITH INDUSTRIAL WATER |  |  |  |  |  |
| Sample: COL. BLUE SEA – DYE WITH TREATED WATER |  |  |  |  |  |
|  | delE | delL | delC | delH | The sample is |
| D65/10 | 0.131 | 0.114 | 0.053 | -0.039 | + clear |
| A/10 | 0.135 | 0.111 | 0.070 | -0.035 | + clear + pure |
| F11/10 | 0.129 | 0.113 | 0.051 | -0.033 | + clear |

DYE WITH REACTIVE DYES (REMAZOL - DYSTAR)

| Formula: CMC 2.0:1.0 |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Substratum: 100% VISCOSE |  |  |  |  |  |  |
| Reference: COL. GREY – DYE WITH INDUSTRIAL WATER |  |  |  |  |  |  |
| Sample: COL. GREY – DYE WITH TREATED WATER |  |  |  |  |  |  |
|  | delE | delL | delC | delH | The sample is |  |
| D65/10 | 0.092 | -0.088 | 0.000 | 0.026 | + dark |  |
| A/10 | 0.117 | -0.087 | 0.020 | 0.075 | + dark |  |
| F11/10 | 0.091 | -0.090 | -0.006 | 0.003 | + dark |  |

| Formula: CMC 2.0:1.0 |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Substratum: 100% VISCOSE |  |  |  |  |  |
| Reference: COL. BLUE SEA – DYE WITH INDUSTRIAL WATER |  |  |  |  |  |
| Sample: COL. BLUE SEA – DYE WITH TREATED WATER |  |  |  |  |  |
|  | delE | delL | delC | delH | The sample is |
| D65/10 | 0.415 | -0.366 | -0.193 | -0.029 | + dark + dirty |
| A/10 | 0.420 | -0.361 | -0.213 | -0.005 | + dark + dirty |
| F11/10 | 0.422 | -0.357 | -0.222 | -0.029 | + dark + dirty |

The variations of tone between the samples dyed in the two types of water are within the acceptable levels of tolerance as recommended in the quality standard norm of the 2003 edition of Italian Textile Association. ( i.e.: delE=1)

##### Colour fastness to washing

grey colour –direct dyes:

|  | dyeING IN industrial water | dyeING IN treated water |
| --- | --- | --- |
| Degradation-colour: | 4-5 | 4-5 |
| Staining on: |  |  |
| Wool | 4-5 | 4-5 |
| Acrylic | 4-5 | 4-5 |
| Polyester | 4-5 | 4-5 |
| Polyamide | 4 | 4 |
| Cotton | 4-5 | 4-5 |
| Acetate | 4-5 | 4-5 |

blue colour –direct dyes:

|  | DYEING IN INDUSTRIAL WATER | DYEING IN TREATED WATER |
| --- | --- | --- |
| Degradation colour: | 4 | 4 |
| Staining on: |  |  |
| Wool | 3-4 | 3 |
| Acrylic | 4-5 | 4 |
| Polyester | 3 | 3 |
| Polyamide | 2-3 | 2-3 |
| Cotton | 1-2 | 1-2 |
| Acetate | 4 | 4 |

The differences in colour fastness expressed are not significant.

grey colour – reactive dyes:

|  | DYEING IN INDUSTRIAL WATER | DYEING IN TREATED WATER |
| --- | --- | --- |
| Degradation colour: | 4 | 4 |
| Staining on: |  |  |
| Wool | 4-5 | 4-5 |
| Acrylic | 4-5 | 4-5 |
| Polyester | 4 | 4-5 |
| Polyamide | 3-4 | 3-4 |
| Cotton | 4 | 3-4 |
| Acetate | 4 | 4-5 |

blue colour – reactive dyes:

|  | DYEING IN INDUSTRIAL WATER | DYEING IN TREATED WATER |
| --- | --- | --- |
| Degradation colour: | 4 | 4 |
| Staining on: |  |  |
| Wool | 4-5 | 4-5 |
| Acrylic | 4-5 | 4-5 |
| Polyester | 4-5 | 4-5 |
| Polyamide | 3-4 | 3-4 |
| Cotton | 3-4 | 3-4 |
| Acetate | 4-5 | 4-5 |

The differences in colour fastness expressed are not significant.

##### Colour fastness to rubbing

| dyeING IN industrial water |  | dyeING IN treated water |  |
| --- | --- | --- | --- |
| colour fastness to rubbing |  | colour fastness to rubbing |  |
| dry | wet | Dry | wet |
| grey colour-direct dyes |  |  |  |
| 4-5 | 4-5 | 4-5 | 4-5 |
| blue sea colour-direct dyes |  |  |  |
| 4-5 | 3 | 4 | 3 |
| grey colour reactive dyes |  |  |  |
| 4-5 | 4-5 | 4-5 | 4-5 |
| blue sea colour-reactive dyes |  |  |  |
| 4-5 | 3 | 4-5 | 3 |

As outlined there is no longer any variation between  colourfastness to rubbing  in the samples dyed in using two types of water.

##### Conclusions: reuse of permeate for scouring and dyeing of viscose

In general the differences revealed at the end of each test is of little significance as they do not indicate any particular problem.

The results obtained with treated water, in reference to the materials used in the  laboratory can be considered equal to those obtained by using industrial water.

## Sulphur dyeing

### Anaerobic biodegradability test

In the experiment carried out with dyeing wastewater that contained a very high amount of VFA (4310 mg/l) and VFA/COD ratio around 74%, the VFA in the wastewater mainly consisted of acetate. However, during experimental time the acetate could not be converted into methane and 5361 mg/l still remained at the end of the experiment. This can be explained by the fact that methanogenic bacteria are inhibited by a pH drop to 5.5 at the end of the experiment. The results reveal that the added NaHCO3 was not enough to buffer the medium. The CODt immediately decreased from 6027 mg CODt/l to 4692 mg CODd/l after addition of sodium carbonate to the medium (sludge, wastewater, nutrients, and trace element) and the minimum concentration was 5378 mg/l at the end. Visual observation showed that precipitation was formulated after added sodium bicarbonate. This was the reason of the decrease of COD from 6027 mg/l to 4692 mg/l at day 0. The concentration of COD-CH4 was increased from 0 to 479 mg/l after 31 days. Granular sludge only needed 1 day to reduce the colour from 0.932 to 0.294 A. The colour remained unchanged until day 4 and then was increased to 0.683 at the last day. Removal efficiency for COD only reached 18-22%. The experimental results are presented in Figure 67 and Figure 68.

Figure 67 - Anaerobic biodegradability of sulphur dyeing wastewater. Filtered COD (x), COD-VFA (∆) and COD-CH4 (○).

Figure 68 - Removal of colour for dyeing wastewater at 616 nm

Effect of initial wastewater concentration on the anaerobic degradability

In the first feed the CODt concentration varied from 2223 to 6539 mg/l. Except in R4 (filtered sample) experiment, the CODd concentration was reduced from 1375-4709 mg/l to 46-362 for 7 days. With the R4 experiment, concentration of COD at beginning was 5885 mg COD/l, and CODd concentration of 836 mg/l still remained after 7 days (Figure 67). R1 (2223 mg COD/l) and R2 (4368 mg COD/l) experiments needed 2 days to reduce COD-VFA concentration from 1326-2829 mg/l to 31-134 mg/l, whereas R3 and R4 needed 7 days to reduce COD-VFA from 4225-4156 to 164-265 mg/l.

Almost all VFA was converted into methane for R1 and R2 experiments. Formation of methane in first day increased very fast from 0 to 1043-1292 mg/l and to maximum 1826-3895 after 7 days. Cumulative methane of R4 and R3 increased from 0 to 5163-5570 COD-CH4 mg/l corresponding to a percentage of methanogenenisation of 86-92% which needed 7 days.

Depending on the change of CODt concentration used in the experiments, colour ranged from 0.8-1.895A for R1, R2, and R3. The result shows that colour was not stable. It increased from 1.610 to 2.640 for R2 and from 1.895 to 4.790A for R3.  With the R1 colour reduced after 2 day from 0.83 to 0.35 and increased again at day 3, 4 and 5 from 0.35 to 0.52 while at the last day of the experiment colour of R1 decreased below 0.34. Colour of R4 was almost insignificant. Colour increased a little bit with effect of turbidity.

The results also show that the pH in all cases increased insignificantly from 7.1 to 7.3 for R1, 7.3 to 7.6 for R2, 7.2 to 7.3 for R3 and decreased from 7.3 below 7.2 for R4 at the end of the experiment. This is explained by the fact that acetate was converted into methane and by release of HCO3-. In the case of R4, a significant amount of VFA remained still in the medium, so pH decreased.

In the second feed the initial CODt concentration was kept at more or less the same value as the first feed. Except in experiment R3, granular sludge needed 7 days to reduce the COD concentration from 1359-4398 mg/l to 43-264 mg/l.  In experiment R4, the anaerobic bacteria were well adapted to the substrate and only needed 7 days to achieve a COD concentration of 264 mg/l. With the same COD concentration as the first feed, experiment R3 needed 9 days to reduce COD from 4153 to 819 mg/l, in this case, sulphur from Na2S may have inhibited anaerobic bacteria or precipitated particles affected contact between sludge and substrate.

Similar to the first feed, COD-VFA, and COD-CH4 gave similar results for R1, R2, and R3, but a longer time was needed for R4.

In the second feed the initial colour could not be kept at the same value. For R1 colour was reduced from 1.270 to 0.565 after 3 days and increased again at day 4 from 0.35 to 0.865 until the end of the experiment. In experiment R2, colour decreased from 1.775 to 0.785 at day 4 and increased up to 1.505 at the last day. The same as for the first feed, in the second feed the colour of R3 increased and decreased in range from 1.500-3.165A. Colour of R4 increased from 0.205 to 0.739 at day 3 and decreased to 0.095 at the end experiment.

The pH remained almost unchanged in all bottles during the experimental period for about one week, pH from 7.4-7.3 for R1, 7.4 to 7.3 for R2, 7.2 to 7.1 for R3 and unchanged at 7.3 for R4.

From the experimental results in Figure 69, it is obvious that the higher COD concentration give a higher anaerobic biodegradability rate, but decolourisation is not achieved with all experiments. For R4 experiment, colour decreased very significant around 85%, but only after using filter paper.

Figure 69 - Biodegradability assay results for dyeing wastewater, for various initial concentrations of COD (mg/l): Initial concentration: 2223 (R1 - x), 4368g (R2 - ○), 6539g (R3 - ∆) and 5885(filter COD) (R4 - ◊). Top: Changes in the total COD concentration, Second: Changes in the COD-VFA concentration, Third: Methane production, Bottom: Colour removal. Bottles received a new feed on day 7.

# Conclusions

The analysis of process effluents reported in this document covers the most important wastewater streams produced in the textile finishing industry and it allows to identify and evaluate all their possible destinies (direct reuse, reuse after on site treatment, direct discharge to WWTP, discharge to WWTP after on site pretreatment…). The elaboration of all these data gained in a Water Pinch assessment, can lead to the definition of optimised water reuse schemes.

On this basis a company can, make preliminary evaluations of water reuse possibilities by using the data reported. In the following the main conclusions for the experimental activities carried out are summarised.

## Anaerobic treatability and feasibility of different textile waste streams

### Dyeing wastewaters

Textile dyeing wastewaters can be pre-treated anaerobically before treatment in a conventional activated sludge plant. Especially for degradation of azo dyes, anaerobic treatment is a good way of rendering the wastewater more susceptible to aerobic treatment. Exhausted dyebaths themselves would probably be too concentrated for treatment, due to toxic concentration of dyestuffs or salts. The latter is especially a concern when treating wastewater of a reactive dyeing process, which often require the usage of large amounts of salt. When water from the rinsing steps of dyeing processes is mixed with the dyebath, concentrations will be lower and treatment will be feasible.

For anaerobic treatment, a co-substrate must be added to the wastewater (see sections 4.6.1.3 and 4.7.1.2). Dye molecules themselves are not readily degradable, but during consumption of the co-substrate by the bacteria in the anaerobic sludge reducing equivalents are released that attack the dye molecules. Successful decolourisation of acid dyeing wastewater and reactive dyeing wastewater has been shown in both batch (see sections 4.6.1.1 and 4.7.1.1) and continuous experiments (see sections 4.6.1.3 and 4.7.1.2). Because of the colour measurement technique using the full UV-VIS spectra, product formation could be observed for the acid dyeing wastewater. This would not have been observed if the conventional maximum absorption wavelength method had been used.

The results for the continuous treatment are mainly indicative. The amount of wastewater was too small to be able to optimise the system and to obtain long-term information on for instance toxicity of the wastewater to the sludge or adsorption of the dyestuff to the sludge. Batch experiments, however, showed good decolourisation. The addition of a redox mediator speeded up the decolourisation process for both wastewaters.

Anaerobic treatment of sulphur dyeing wastewater was only evaluated in batch experiments, and the results indicate that the water probably can better be treated differently. No decolourisation was observed for all tested concentrations. This has probably to do with the dyestuff being insoluble. COD removal and methane production, however, did take place (see section 4.9).

### Indigo dyed cotton scouring wastewater

Wastewater from the scouring of indigo dyed cotton did not give conclusive results (see section 4.3.1.1.2). Possibly, some toxic effect did play a role. Decolourisation was difficult to measure, and results varied for different incubations. The high solids content of the wastewater can have played a role in this. Reduction of the COD concentration was also not observed in all incubations, whereas VFA and methane production looked promising. More tests are needed to determine whether anaerobic treatment is suitable for this type of wastewater.

### Bleaching wastewater

In the anaerobic degradability test, the COD present in the wastewater was converted rapidly into VFA (see section 4.3.1.1.3). Further conversion to methane was not complete, probably due to a toxic effect of the wastewater. Results of the test for the effect of the initial wastewater concentration on the anaerobic degradability were more promising. However, a second feeding resulted in less conversion. Bleaching wastewater is probably toxic to bacteria in anaerobic sludge.

### Sizing liquid

Batch treatment of sizing liquid in a concentration of approximately 4500 mg COD/l was possible. All COD was converted to methane in 18 days. Reactor experiments showed that successful treatment of diluted sizing liquid (around 2000 mg COD/l) in a UASB reactor is only possible at a high enough hydraulic retention time (HRT) of 12 hours. At shorter HRTs the sludge started floating due to accumulating long chain fatty acids covering the granules. Undiluted sizing liquid is very concentrated (around 65000 mg COD/l), and anaerobic treatment of this stream is not feasible.

## Anaerobic treatment of a combination of textile waste streams

Experiments indicated that anaerobic treatment is feasible for the combination of textile waste streams. Size liquid was tested as co-substrate for dyeing wastewater decolourisation. Results were practically the same as for VFA/Glucose as co-substrate. The latter is often used in laboratory testing because as co-substrate it is very effective. Reactor tests showed that anaerobic treatment of size liquid is not feasible, and that for treatment of dyeing wastewaters a co-substrate is needed. Mixing of sizing liquid with the rest of the wastewater of a plant increases the COD load very much, although the volume of the sizing waste stream is very small. Combining sizing and dyeing waste streams can be a good way of diminishing the COD load of the overall wastewater and obtaining a cheap co-substrate for anaerobic treatment.

## Anaerobic pre-treatment for membrane treatment and discharge of membrane concentrates

Membrane treatment tests were performed with anaerobically pre-treated water. Two streams were investigated, the acid dyeing stream and the reactive dyeing stream. Anaerobic treatment of those streams is described in sections 4.6.1.3 and 4.7.1.2. Results of the combined treatment were not better in terms of permeate quality than that membrane treatment alone. This can be explained by the fact that anaerobic treatment of dyeing wastewater does not really remove the dyestuff COD. It was hypothesised that anaerobic treatment could take care of the colour removal, making it easier for membrane treatment to render a colourless permeate. Dyestuff molecules are merely converted and for azo dyes the conversion means they are split in two parts. Smaller molecules can pass a membrane more easily. Additionally, the original dyestuff colour was removed from the wastewater but it still contained some colour due to the colour of the conversion products. After some time in storage, the water became more coloured. This was probably due to the formation of new coloured molecules from treatment products.

When treating on a membrane the effluents anaerobically pretreated, the affinity membrane/effluent, the effect of concentration and the fouling tendency are improved  with respect to the non pre-treated effluent. Nothwithstanding the notably better quality of the effluents after the anaerobic treatment, especially in the colour content, the removals obtained on membranes are sensibly lower than the ones encountered in the raw effluents filtration. The quality of the final permeate therefore is not superior to the one obtained with direct filtration of the non pre-treated effluent.

Under the conditions applied in these experiments, anaerobic treatment is not promising as a pre-treatment for membrane filtration.

Membrane treatment of raw effluents to obtain reusable water is feasible for many streams. The produced concentrates, however, have to be discharged in some way. Treatment of those concentrates is very difficult and costly. The concentrates resulting form the membrane treatment of the anaerobically pre-treated wastewater have been tested respirometrically for their aerobic degradability (see sections 4.6.3 and 4.7.3). For the acid dyeing wastewater it was found that the aerobic degradability of the original wastewater was practically zero, whereas the anaerobic effluent did show some degradability. In contrast to the wastewater, the membrane concentrates were aerobically biodegradable. For the reactive dyeing wastewater the effect was less obvious. This experiment indicates that although anaerobic pre-treatment does not lead to improved results for the membrane treatment in terms of permeate quality (see section 5.2), it might be a good way of producing aerobically biodegradable concentrates that possibly can be discharged to a wastewater treatment plant. As the tests performed within this study were very limited, more research should be done to explore the possibilities.

## Feasibility of membrane treatment

### UF treatment

The UF treatment alone does not normally assure a quality of the permeates suitable for undifferentiated reuse. Permeate flows are high (typically 100 - 150 l h-1 m-2) and costs are affordable (typically 0.30 - 0.40 Euro/m3 in the hypothesis of 50,000 m3/year of water to be treated) but organics and colour removal are variable and conductivity is not affected.

### NF treatment

NF resulted to be the best compromise between the need of having high flow rates (consequently reducing treatment costs) and good quality permeates. The colour is almost completely removed and residual values never affect the reusability. The salinity abatement is variable and in the effluents of certain dyeing operation (i.e. reactive dyeing of silk and cotton), where mono-valent salts are used heavily, the removal is low and it prevents the reuse. The removal of organic matter is high, typically 80 -90%, nevertheless effluents with a high organic content (DOC> 400-500 mg l-1) give permeates normally not reusable.

Direct NF treatment resulted feasible only on the most diluted effluents of rinsing operations. The percentage removals in these cases are lower but sufficient to produce a permeate reusable in any process. Costs are also promising, ranging between 0.55 and 0.68 euro/year in a scenario of 50,000 m3/year of effluent to be treated.

The treatment configuration UF + NF seems in most cases technically and economically feasible except for the silk polymer charge, polyester double scouring and cotton bleaching line which evidenced very low permeate fluxes and/or relevant material accumulation on the membrane surface. In the hypothesis of 50,000 m3/year of water to be treated, the cost range would be 0.67 –0.83 euro/year.

### RO treatment

RO treatment of the tested effluents always required an UF pre-treatment and despite the very high removal of contaminants, it resulted to be scarcely promising because of the very low fluxes (<10 l h-1 m-2) and, consequently, high costs (1,60-2,90 Euro/m3).

## Reusability evaluations

The quality evaluation of the textile material has always been linked to the differences in water quality: fresh process water versus permeate. Concerning organic pollution and colour no differences were detected. The membrane filtration however had no effect on the pH and the conductivity of the water when it is related to monovalent salts. This means that waste water containing a high content of NaCl results in a permeate with a comparable concentration. Since NaCl regulates the speed and the depth of reactive and direct dyeing of cotton, a higher concentration has a significant effect on the colour of the dyed cotton. The fabric dyed with permeate has a deeper colour shade since the reactive dyestuff are more exhausted thanks to the higher concentration of NaCl in the permeate.

The fastness properties were not negatively influenced. The pH of the permeate is easy to adapt, the salt content however is not easy to change.

On the other hand, textile processes in which little or no salt (NaCl) is dosed, the quality of the permeate is comparable to fresh process water and the quality of the treated (pre-treatment/dyeing) textile material is as good as the reference. As an example the dyed polyester fabric is shown in. No significant colour differences can be noticed.

As a conclusion we can state that the permeate of UF/NF or NF only, can be re-used for pre-treatment and/or dyeing of some of the most used textile raw materials, i.e. polyester, polyamide, silk, viscose. The presence of salt (NaCl) however hampers the re-usability for the dyeing of cotton.