Content of Deliverables:

1	Introduction	4

2	Description of the activities	5

3	Methodology of WaterPinch	6

3.1	From PIDACS towards data sheets	6

3.2	Selection of reusable process effluents & Calculations	7

3.3	Information used from test results	8

3.4	Visualisation and optimization	9

4	Alternative water schemes for screened companies	11

4.1	Company B01	11

4.1.1	Production	11

4.1.2	Water balance	11

4.1.3	Selection of reusable process effluents & used test results	11

4.1.4	Obtained water savings	12

4.1.5	Changed contamination of process water & discharges	12

4.1.6	Economical evaluation	13

4.2	Company B02	14

4.2.1	Production	14

4.2.2	Water balance	14

4.2.3	Selection of reusable process effluents & used test results	14

4.2.4	Obtained water savings	14

4.2.5	Changed contamination of process water & discharges	14

4.2.6	Economical evaluation	14

4.3	Company B04	15

4.3.1	Production	15

4.3.2	Water balance	15

4.3.3	Selection of reusable process effluents & used test results	15

4.3.4	Obtained water savings	16

4.3.5	Changed contamination of process water & discharges	16

4.3.6	Economical evaluation	17

4.4	Company B05	18

4.4.1	Production	18

4.4.2	Water balance	18

4.4.3	Selection of reusable process effluents & used test results	18

4.4.4	Obtained water savings	19

4.4.5	Changed contamination of process water & discharges	19

4.4.6	Economical evaluation	20

4.5	Company I04	21

4.5.1	Production	21

4.5.2	Water balance	21

4.5.3	Selection of reusable process effluents & used test results	21

4.5.4	Obtained water savings	22

4.5.5	Changed contamination of process water & discharges	23

4.5.6	Economical evaluation	24

4.6	Company I06	25

4.6.1	Production	25

4.6.2	Water balance	25

4.6.3	Selection of reusable process effluents & used test results	25

4.6.4	Obtained water savings	27

4.6.5	Changed contamination of process water & discharges	27

4.6.6	Economical evaluation	28

4.7	Company I09	29

4.7.1	Production	29

4.7.2	Water balance	29

4.7.3	Selection of reusable process effluents & used test results	29

4.7.4	Obtained water savings	30

4.7.5	Changed contamination of process water & discharges	31

4.7.6	Economical evaluation	31

4.8	Company I15	33

4.8.1	Production	33

4.8.2	Water balance	33

4.8.3	Selection of reusable process effluents & used test results	33

4.8.4	Obtained water savings	35

4.8.5	Changed contamination of process water & discharges	35

4.8.6	Economical evaluation	37

5	General conclusions	38

# Introduction

The work documented in this report is part of the project “Evaluation of the effluent of the IPPC application on the sustainable waste water management in the textile industries (Towef0)” funded by the European Commission as a shared cost RTD project in the 5th Framework Research program, Energy, Environment and Sustainable Development, Key action 1 Sustainable management and Quality of Water, Treatment and purification technologies, Waste water treatment and reuse.

The project objective is to establish a multicriteria integrated and coherent implementation of Good Environmental Practices (GEP) and to promote the efficiënt use of resources within textile finishing industries characterised by large use of water, taking into account the treatment of industrial waste water effluent (Urban Waste Water Treatment  Directive 91/271 EEC) and the impact of the final discharge to the water recipient bodies (Water Framework Directive COM (98)).

Partners of the project were: ENEA, the Italian National Agency for New Technologies, Energy and the Environment, Vito, a Belgian Research centre for the industry, Centexbel, a research centre for the Belgian textile federation, the Joint Research Centres of Siviglia and Ispra, Lariana Depur S.p.A., a private Italian company, Ecobilan, a private French company and Environmental Protection & Resource Conservation Foundation (EP&RC).

Within this project several Italian and Belgian companies were screened. Useful information for further evaluation was put into Process Identification & Data Collections Sheets (PIDACS) by Lariana and Centexbel.

These data were furthermore used by Vito to design alternative water schemes for different textile finishing companies, in order to minimise water consumption in a cost effective way.

This document gives a detailed overview of the results obtained within Work-Package 4: WaterPinch technology in textile finishing industries (silk, synthetic fibres and cotton).

# Description of the activities

The main objective of this part of the project was to design alternative water schemes for different textile finishing companies, in order to minimise water consumption in a cost effective way.

WP 4 was split into seven job cards:

WP04.01.4		Methodology for waterpinch technology application on textile industry

WP04.02.4		Definition of the criteria for the textile processes identification

WP04.03.4		Definition of the criteria for identification of water reuse options.

WP04.04.4		Definition for the collection and elaboration of process data.

WP04.05.4		Design of water reuse scheme and definition of necessary water quality.

WP04.06.4		Design of database of allowable inlet concentrations of the textile processes.

WP04.07.4		Guidelines for an optimal reduction of water usage and discharge

In addition one job-card from WP5 is linked to this issue:

WP05.07.4		Integrated methodology for waterpinch and waste water design

The results of these job-cards are summarised in this document, covering following three deliverables:

Deliverable 8	Data source on relaxation possibilities of process inlet water quality.

Deliverable 9	Optimal water re-use procedures applicable in the synthetic/silk/cotton industry.

Deliverable 14	Integrated methodology for waterpinch and waste water design.

The three deliverables are merged into one document as their content is clearly linked.

This document starts with the methodology used to optimise the water schemes of the different evaluated companies. It explains how the information from the other work packages was used. Test results from membrane filtration trials, as well as economical evaluations done by ENEA were integrated into the schemes. Furthermore, indicative values are given on relaxation possibilities for different process steps.

Attached in annex all detailed information about the optimised water schemes of the different industries can be found.

# Methodology of WaterPinch

This part describes the different steps of the methodology that was used starting from the company-specific PIDACS till the design of an alternative water scheme in the dedicated software WaterTracker®.

## From PIDACS towards data sheets

Starting from the PIDACS, the elaborated amount of data needed to be compiled into a surveyable format. All the useful information with regard to water minimization was extracted and summarized  into Excel data sheets. The way the information was presented is illustrated in Figure 1.

Figure 1  : Data sheets containing all relevant information for water minimization

The following information is found in these tables:

- Process number and name as used in the PIDACS.

- Fabric on which this process is done.

- Machine on which this process is done.

- Number and name of the sub-sequence as used in the PIDACS.

- Water consumption & discharge for the different types of water.

- Contamination of the discharge.

These tables were used for preliminary,  summarizing calculations: Waste waters from similar processes were grouped and their mixed flow rate and contamination was calculated. By grouping these similar flows, the amount of information to be entered into the visualisation software is reduced significantly.

## Selection of reusable process effluents & Calculations

The selection of the streams was based on the experimental results from the membrane filtration trials and the reuse tests.

The main criteria to select streams for reuse can be generalized as follows:

- No pretreatment or dye baths taken into consideration. These streams are often too concentrated for treatment by membrane filtration.

- The upper limit for the COD value is set at 1000 mg /l in order to reach, after filtration, sufficient low values for reuse of permeate. However, for some specific cases another limit was used. This is discussed further in the detailed descriptions of the different cases.

- The conductivity is preferable lower than 1000 µS /cm. This is important in case of reactive and sometimes acid and direct dyeing, where salt content plays a crucial role on the dyeing recipe. For other dyeing processes it can be expected that conductivity will anyway be below this value.

As a result, the different process effluents are grouped into non reusable - high contaminated discharges and reusable - low contaminated flows.

Pretreatment, dyeing and finishing departments were evaluated separately as they are often situated at different locations.

Figure 2 illustrates how calculations were done in the data sheets. Contamination of the grouped process effluents is determined. As explained in paragraph 3.1 these calculations were done in order to group similar process-effluents to reduce the amount of information to be entered into the visualisation software.

Figure 2 : Summarizing calculations in data sheets

## Information used from test results

The identification of reuse/recycle options of process effluents implies a knowledge of the maximum tolerated relaxation of the inlet water quality . Specific data for textile processes was gathered from literature data and from partners know-how. Table 1 gives a non-exhaustive, qualitative list of possible relaxation -of the inlet water qualities- and reuse for different steps in a textile finishing company. Some quantitative ranges are given as well.

Table 1 : Possible reuse and relaxation for different process streams

| Process | Effluent | Relaxation |
| --- | --- | --- |
| Desizing | Possible product recovery. Permeate recyclable. | Low quality water accepted. |
| Prewashing | Possible regeneration. | Low quality water accepted |
| Bleaching | Possible reuse of rinsing waters. Regeneration could be required. | High quality required (COD<60mg/l and S.S.<5mg/l) |
| Mercerising | Recovery of NaOH |  |
| Dyeing | Possible reuse of rinsing waters. Regeneration could be required. | High quality required (COD<60mg/l and S.S.<5mg/l) |
| Printing | Possible reuse of rinsing waters. Regeneration could be required. | High quality required (COD<60mg/l and S.S.<5mg/l) |

Due to the vast variation in textile processes and related effluents it is very hard to generalize the required inlet concentrations of the different steps. The values of Table 2 are used as reference general requirements for process water in the Belgian textile industry and have also been agreed with Italian industrial representatives.

Since the required quality is subjected to multiple parameters like the product colour (light or dark), the type of  rinsing (first or final), the kind of dyestuff that is being used… extensive testing is still required for every specific case.

Table 2 :Generalized process water requirements

| Parameter | Value |
| --- | --- |
| pH | 6.5 – 9 |
| Hardness (°F) | < 5 |
| Conductivity (µS/cm) | < 1 000 |
| COD (mg/l) | < 60 |
| Fe (µg/l) | < 100 |
| Mn (µg/l) | < 100 |
| Colour | No visible colour or suspended solids |

Secondly, results from the membrane filtration trials and the anaerobic lab test were used as a basis for the removal efficiency values of the introduced technologies in the software package WaterTracker®.

Only 17 different process effluents from the screened companies were tested. As a result, assumptions had to be made based on interpolations of these values for all other optimizations.

Finally, the economic evaluation of the effluent treatment was used as an additional guideline for the optimization. It was illustrated that the higher the flow rate through the membrane filtration unit, the lower the cost per m³ treated water. However, above 50 000 m³ /year the cost decrease becomes minor. This is clearly illustrated in the figure below.

Figure 3 :Example of a cost curve for membrane treatment (combination UF-NF)

## Visualisation and optimization

Based on the data sheets and calculations, the water network was visualized in the dedicated software WaterTracker® from Linnhoff March. Flow rates and concentrations of contaminations are entered. The software now calculates the overall water consumption and contaminiation of the final discharges.

Finally, all schemes were optimised by implementation of membrane filtration technology and anaerobic end-of-pipe treatment plant. Results from trials, reuse tests and economical evaluations were taken into account as described in previous paragraph 3.3.

The water saving potential, compared to the initial situation, was calculated by the software. Furthermore, the impact on the water quality parameters of the feed stream towards the processes (due to mixture with membrane permeate) was determined, as well as the increased contamination of the final effluent, as a result of the obtained water saving.

All this is illustrated in Figure 4.

Figure 4 : Extract of water circuit optimization using WaterTracker®

# Alternative water schemes for screened companies

The methodology, as explained above, was applied to eight of the screened Italian and Belgian companies. The specific approach for each company, as well as the obtained results are reported in this chapter . All detailed data sheets and WaterTracker® schemes can be found in Annex 1 and 2.

## Company B01

### Production

Table 3 illustrates some production values as can be found in the PIDACS.

Table 3 : Production values B01

| Fiber | Type | Production |  |
| --- | --- | --- | --- |
| Polyester | yarn dyeing | 465 000 | kg /yr |
|  | piece dyeing | 855 000 | kg /yr |
| Total |  | 12 408 000 | kg /yr |

The optimization was focused on the commission finishing of polyester.

### Water balance

In production ground water is used. The overall water consumption is 857 839 m³ /yr, according to the PIDACS.

The water consumption of the evaluated polyester processes is 48 150 m³ /yr.

The detailed water balance can be found in Annex 1 and 2.

### Selection of reusable process effluents & used test results

In reference to the membrane filtration trial PDD/UF/NF the removal efficiency of a combined UF/NF on disperse dyeing effluents is as indicated in Table 4.

Table 4 : Removal efficiencies on disperse dyeing effluents

| UF/NF | Removal |  |
| --- | --- | --- |
| Organic fraction | 53 | % |
| Conductivity | 49 | % |
| TSS | 99 | % |

In addition, it is assumed that for a combined ultra- and nano-filtration plant a recovery up to 80% should be achievable.

All rinsing phases were selected for reuse. Parameters of those streams are as indicated in Table 5.

Table 5 : Selection of reusable streams B01

| Criterion |  |  |
| --- | --- | --- |
| COD | < 2 000 | mg /l |
| Conductivity | < 2 500 | µS /cm |

These criteria are slightly different than those given in the methodology. However, tests have proven that permeate from a combined UF/NF filtration on rinsing effluents from disperse dyeing processes can be reused in a similar process.

### Obtained water savings

The water consumption in the initial situation for the screened processes was 48 150 m³ /yr.

Using the above selection criteria and removal efficiencies of the implemented membrane filtration technology, the water consumption for the specific polyester dyeing processes is reduced to           30 750 m³ /yr. This reduction equals 36%.

The flow rate towards the UF/NF installation will be 21 750 m³ /yr.

Details are given in Annex 2.

### Changed contamination of process water & discharges

Table 6 summarizes the contamination of the process water for the initial and alternative scenario’s.

Table 6 : Process water quality B01

| Stream | Temperature | Conductivity | COD | TSS |
| --- | --- | --- | --- | --- |
|  | °C | µS /cm | mg /l | mg /l |
| Ground water | 16 | 910 | 10 | 0 |
| Permeate UF/NF | 39 | 870 | 438 | 0 |
| Mix permeate & ground water | 24 | 890 | 164 | 0 |

It can be concluded that the obtained COD concentration, after mixing the permeate with ground water is significantly higher than the general process water quality as indicated in chapter 3.3.

However, tests have proven that permeate from a combined UF/NF filtration on rinsing effluents from disperse dyeing processes can be reused in a similar process.

As the water consumption decreases, the contamination of the final effluent increases proportionally.

These changes are illustrated in Table 7.

Table 7 : Changed effluent concentration B01

| Stream | Temperature | Conductivity | COD | TSS |
| --- | --- | --- | --- | --- |
|  | °C | µs /cm | mg /l | mg /l |
| Initial effluent | 61 | 3 350 | 2 513 | 144 |
| Effluent after optimization | 74 | 4 800 | 3 740 | 228 |

### Economical evaluation

Using the economical evaluation done by ENEA for a combined UF/NF treatment on a disperse dyeing effluent it can be concluded that the costs for this specific regeneration technology on a process effluent of 21 750 m³ /yr is around € 1.2 /m³.

Compared to the actual cost of ground water of  € 0.12 /m³ this is still very high.

Increasing costs for groundwater, as well as more stringent limits on the use of it, however will stimulate the search for alternative process water.

Besides the mentioned reduced cost of € 0.12 /m³ groundwater, the decrease of energy consumption for pumping water to and from the process should be evaluated as well.

## Company B02

### Production

Table 8 illustrates some production values as can be found in the PIDACS.

Table 8 : Production values B02

| Fiber | Type | Production |  |
| --- | --- | --- | --- |
| Cotton | yarn or fabric |  |  |
| Polyester | yarn |  |  |
| Total |  | 16 777 000 | kg /yr |

The evaluation was focused on the piece and yarn pretreatment and dyeing of cotton.

### Water balance

In production ground water is used. The overall water consumption is 396 510 m³ /yr, according to the PIDACS.

The water consumption of the evaluated cotton processes is 288 211 m³ /yr.

The detailed water balance can be found in Annex 1.

### Selection of reusable process effluents & used test results

All measured rinsing effluents are highly contaminated. In addition, no membrane filtration test results are available for vat, sulphure and indigo dyeing. As a result, no alternative water circuits were suggested.

### Obtained water savings

Not relevant

### Changed contamination of process water & discharges

Not relevant.

### Economical evaluation

Not relevant.

## Company B04

### Production

Table 9 illustrates some production values as can be found in the PIDACS.

Table 9 : Production values B04

| Fiber | Type | Production |  |
| --- | --- | --- | --- |
| Cotton | yarn dyeing | 1 463 200 | kg /yr |
|  | fabric dyeing | 5 852 800 | kg /yr |
| Total |  | 7 316 000 | kg /yr |

The optimization was focused on the reactive dyeing, both of cotton yarn and pieces.

### Water balance

In production mainly ground water is used. However, for steam production rain water is captured.  The overall ground water consumption is around 553 073 m³ /yr, according to the PIDACS.

The ground water consumption as obtained in the WaterTracker® scheme is 478 439 m³ /yr. This is slightly different from the total water consumption as mentioned in the PIDACS. The reason for this difference is that the overall value is based on flow meters and the water scheme value on the summation of all the different processes taken into account. As a result the small water losses due to manual operations and cleaning processes are not counted.

The detailed water balance can be found in Annex 1 and 2.

### Selection of reusable process effluents & used test results

In reference to the membrane filtration trial CRD/UF/NF the removal efficiency of a combined UF/NF on cotton reactive dyeing process effluents is as indicated in Table 10.

Table 10 : Removal efficiencies on reactive dyeing effluents

| UF/NF | Removal |  |
| --- | --- | --- |
| Organic fraction | 84 | % |
| Conductivity | 15 | % |
| TSS | 99 | % |

In addition, it is assumed that for a combined ultra- and nano-filtration plant recoveries up to 80% should be achievable.

Water seals, rinsing, soaping, fixation and softening phases were selected for reuse. Parameters of those streams are as indicated in Table 11.

Table 11 : Selection of reusable streams B04

| Criterion |  |  |
| --- | --- | --- |
| COD | 1 500 | mg /l |
| Conductivity | < 5 000 | µS /cm |

These criteria are different from those given in the methodology. It was shown during membrane filtration trials (on total process effluent, including dye bath) and reuse tests that the regeneration and reuse of reactive dyeing effluents is difficult. The pH and salt concentration are too high. Adjustment of pH is easily achievable. However, as the conductivity appeared to be too high during the tests, no dye baths were included during this optimization.

### Obtained water savings

Compared to the initial value of 478 439 m³ /yr, the obtained water consumption after optimization is 364 169 m³ /yr. This reduction equals 24%.

The flow rate towards the UF/NF installation will be 122 126 m³ /yr.

Details are given in Annex 2.

### Changed contamination of process water & discharges

Table 12 summarizes the contamination of the process water for the initial and alternative scenario’s.

Table 12 : Process water quality B04

| Stream | Temperature | Conductivity | COD | TSS | Hardness |
| --- | --- | --- | --- | --- | --- |
|  | °C | µS /cm | mg /l | mg /l | °F |
| Ground water before pretreatment | 15 | 1 109 | 27 | 0 | 53 |
| Ground water after pretreatment | 15 | 1 109 | 27 | 0 | 2 |
| Permeate | 51 | 4 210 | 83 | 0 |  |
| Mix permeate & ground water | 24 | 1 850 | 40 | 0 |  |

The obtained conductivity of the mix permeate and ground water is higher than the process water criteria as mentioned in chapter 3.3. The impact of the salt concentration on the recipe should be evaluated.

As the water consumption decreases, the contamination of the final effluent increases proportionally.

These changes are illustrated in Table 13.

Table 13 : Changed effluent concentrations B04

| Stream | Conductivity | COD | TSS |
| --- | --- | --- | --- |
|  | µs /cm | mg /l | mg /l |
| Effluent before treatment - initial | 5 220 | 2 590 |  |
| Effluent after treatment - initial | 5 220 | 699 | 30 |
| Effluent before treatment - optimized | 5 500 | 3 800 |  |
| Effluent after treatment - optimized | 5 500 | 1 000 | 30 |

The concentration of TSS after an aerobic biological treatment will be around 30 ppm if no problems occur. Temperature will be within the range of 15 to 25°C.

It can be assumed that the COD concentration after the biological treatment will be lower than calculated at the same initial removal rate of the activated sludge. As the hydraulic load of the system will increase, the efficiency will probably increase. Tests however are required.

### Economical evaluation

Using the economical evaluation done by ENEA for a combined UF/NF treatment on a reactive dyeing effluent it can be concluded that the costs for a regeneration technology on a process effluent of 97 700 m³ /yr is around € 0.69 /m³.

This should be compared to the actual cost of groundwater plus the costs for the treatment of the ground water. In case of company B04 this equals € 0.05 /m³ ground water & € 0.32 for the combined de-ironing and softening or € 0.37 /m³ in total.

## Company B05

### Production

Table 14 illustrates some production values as can be found in the PIDACS.

Table 14 : Production values B05

| Fiber |  | Production |  |
| --- | --- | --- | --- |
| Natural fibers | cotton and flax | 50 | % |
| Mixed fibers | cotton in combination with polyester, polyamide, flax, wool or viscose | 50 | % |
| Total |  | 6 300 000 | kg/yr |

All processes were screened for possible optimization.

### Water balance

In production mainly ground water is used. The water consumption is 500 000 m³ /yr according to the PIDACS.

The ground water consumption as obtained in the WaterTracker® scheme is 242 353 m³ /yr. This value is based on what can be expected from the summation of the different process steps, but is significantly lower than the measured consumption.

As a result, more than 50% of the water consumption cannot be determined correctly. Equipment washing explains often an important part of this consumption.

The detailed water balance can be found in Annex 1 and 2.

### Selection of reusable process effluents & used test results

Refering to the membrane filtration trial PDD/UF/NF the removal efficiency of a combined UF/NF on Polyester disperse dyeing process effluents are as indicated in Table 15.

It was assumed that for a combined vat/disperse dyeing waste water similar removal efficiencies can be obtained as for a polyester disperse dyeing effluent.

Table 15 : Removal efficiency for disperse dyeing effluents

| UF/NF | Removal |  |
| --- | --- | --- |
| Organic fraction | 53 | % |
| Conductivity | 50 | % |
| TSS | 99 | % |

In addition, it is assumed that for a combined ultra- and nano-filtration plant a recovery up to 80% should be achievable.

Table 16 : Selection of reusable streams B05

| Criterion |  |  |
| --- | --- | --- |
| COD | < 1 000 | mg /l |
| Conductivity | < 5 000 | µS /cm |

The limit for conductivity is different from the one given in the methodology. However, tests have proven that permeate from a combined UF/NF filtration on rinsing effluents from disperse dyeing processes can be reused in a similar process.

In addition, an anaerobic treatment is suggested as a decolourization step for the waste water coming from the reactive dyeing processes (in case of AZO-dyes).

The possible removal efficiency of an anaerobic reactor on reactive dyeing waste water was tested by LeAF. Lab trials showed that a good decolourization and a COD removal of 30% is achievable. The conductivity is assumed to be unchanged. Temperature of the anaerobic effluent will be around 35°C and the TSS of a good working reactor should be around 200 mg /l.

In order to add sufficient organic carbon to the process, those effluents with a high BOD/COD value from the bleaching line should be mixed with the reactive dyeing waste water before adding to the treatment.

### Obtained water savings

Compared to the initial value of 242 353 m³ /yr, the obtained water consumption after optimization is 187 214 m³ /yr. This reduction equals 23%.

Details are given in Annex 2.

### Changed contamination of process water & discharges

Table 17 summarizes the contamination of the process water for the initial and alternative scenario’s.

Table 17 : Process water quality B05

| Stream | Temperature | Conductivity | COD | TSS |
| --- | --- | --- | --- | --- |
|  | °C | µs /cm | mg /l | mg /l |
| Treated ground water | 15 | 1 000 | 0 | 0 |
| Permeate UF/NF | 42 | 1 470 | 196 | 0 |
| Mix permeate and ground water | 26 | 1 200 | 82 | 0 |

It can be concluded that the obtained COD and conductivity concentration, after mixing the permeate with ground water are slightly higher than the general process water quality as indicated in chapter 3.3.

However, tests have proven that permeate from a combined UF/NF filtration on rinsing effluents from disperse dyeing processes can be reused in a similar process.

As the water consumption in the dyeing department decreases, the contamination of its effluent increases.

On the other hand, when an anaerobic reactor is implemented in the scheme on some specifice process effluents, the COD of the final effluent will be reduced again partly.

These changes are summarized in Table 18.

Table 18 : Changed effluent concentraion B05

| Stream | Temperature | Conductivity | COD | TSS |
| --- | --- | --- | --- | --- |
|  | °C | µs /cm | mg /l | mg /l |
| Initial effluent | 63 | 4 530 | 2 029 | 27 |
| Effluent after optimization | 60 | 5 630 | 2 445 | 72 |

### Economical evaluation

Using the economical evaluation done by ENEA for a combined UF/NF treatment on a disperse dyeing effluent it can be concluded that the costs for this specific regeneration technology on a process effluent of 65 478 m³ /yr is around € 0.7 /m³.

This is comparable to the actual cost of ground water of € 0.75 /m³ (including treatment costs).

As a result, it is proven that in cases of high costs of ground water treatment the implementation of a membrane filtration technology can offer an achievable solution.

## Company I04

### Production

Table 19 illustrates some production values as can be found in the PIDACS.

Table 19 : Production values I04

| Fiber | Type | Production |  | % on total |  |
| --- | --- | --- | --- | --- | --- |
| Bemberg | Fabric | 789 880 | kg /yr | 15.59 | % |
| Mix acetate | Fabric | 1 476 300 | kg /yr | 29.13 | % |
| Viscose | Fabric | 1 776 320 | kg /yr | 35.06 | % |
| Total |  | 5 067 160 | kg /yr |  |  |

The total company was screened for optimization.

### Water balance

In production well water, as well as industrial water is used. The industrial water consumption equals 229 112 m³ /yr and the well water use equals 335 025 m³ /yr according to the PIDACS.

The well water consumption as obtained in the WaterTracker® scheme is 318 484 m³ /yr. This is slightly different from the water consumption as mentioned in the PIDACS. The reason for this difference is that the overall values are based on flow meters and the water scheme values on the summation of all the different processes taken into account. As a result the small water losses due to cleaning processes etc… are not counted.

The detailed water balance can be found in Annex 1 and 2.

### Selection of reusable process effluents & used test results

The removal efficiency of a combined UF/NF on waste water coming from scouring processes is based on the membrane filtration trials PDS/UF/NF and PS/UF/NF. The used values are illustrated in Table 20.

Table 20 : Removal efficiencies on scouring effluents (weighted average)

| UF/NF | Removal |  |
| --- | --- | --- |
| Organic fraction | 80 | % |
| Conductivity | 80 | % |
| TSS | 99 | % |

In addition, it is assumed that for a combined ultra- and nano-filtration plant a recovery up to 80% should be achievable.

Furthermore, the removal efficiency of a combined UF/NF on the mix of several dyeing process effluents was based on following list of membrane filtration tests:

- Direct dyeing rinsing phase:	VDDR/NF		(viscose)

- Disperse dyeing:		PDD/UF/NF	(polyester)

- Reactive printed washing phase:	VRPW/UF/NF

The obtained averages, based on these data are illustrated in Table 21.

Table 21 : Removal efficiencies on dyeing effluents (weighted average)

| UF/NF | Removal |  |
| --- | --- | --- |
| Organic fraction | 44 | % |
| Conductivity | 42 | % |
| TSS | 99 | % |

For the pretreatment section the selection criteria are as indicated in Table 22.

Table 22 : Selection of reusable streams preparation I04

| Criterion |  |  |
| --- | --- | --- |
| COD | < 1 000 | mg /l |
| Conductivity | < 1 000 | µS /cm |
| Other | no doping phases |  |

For the dyeing department the selection criteria are as indicated in Table 23.

Table 23 : Selection of reusable streams dyeing I04

| Criterion |  |  |
| --- | --- | --- |
| COD | < 1 000 | mg /l |
| Conductivity | < 1 000 | µS /cm |
| Other | no baths no rinsing waters when difficult to separate from concentrated baths |  |

These criteria are similar to the values given in the methodology.

### Obtained water savings

The total water consumption in production in the initial situation was 547 596 m³ /yr. It is assumed that the industrial water use is constant at 229 112 m³ /yr.

As a result, the well water consumption is reduced from 318 484 m³ /yr to 157 026 m³ /yr after optimizing the water circuit.

These values correspond to a reduction of 50.7% for the well water and 29.4% for the total water consumption in production.

The flow towards the UF/NF unit in the preparation section equals 88 810 m³ /yr.

In the dyeing department, the treated flow rate is slightly higher and equals 113 012 m³ /yr.

Details are given in Annex 2.

### Changed contamination of process water & discharges

Table 24 summarizes the contamination of the process water for the initial and alternative scenario’s in the pretreatment department.

Table 24 : Process water quality in preparation section I04

| Stream | Temperature | Conductivity | COD | TSS |
| --- | --- | --- | --- | --- |
|  | °C | µs /cm | mg /l | mg /l |
| Process water (mix of well water industrial water and permeate of existing NF) | 17 | 360 | 10 | 0 |
| Permeate UF/NF | 24 | 50 | 80 | 0 |
| Mix permeate & process water | 20 | 230 | 40 | 0 |

In addition, Table 25 summarizes the contamination of the process water for the initial and alternative scenario’s in the dyeing department.

Table 25 : Process water quality in dyeing department I04

| Stream | Temperature | Conductivity | COD | TSS |
| --- | --- | --- | --- | --- |
|  | °C | µs /cm | mg /l | mg /l |
| Process water (mix of well water industrial water and permeate of existing NF) | 17 | 360 | 10 | 0 |
| Permeate UF/NF | 24 | 160 | 155 | 0 |
| Mix permeate & process water | 20 | 270 | 73 | 0 |

It can be concluded that COD of the mix of permeate & process water is slightly higher than the value of 60 mg /l as mentioned in the methodology. This could imply problems for reuse. As a result, specific reuse tests would be required.

As the water consumption decreases, the contamination of the final effluent increases proportionally.

These changes are illustrated in Table 26.

Table 26 : Changed effluent concentration I04

| Stream | Temperature | Conductivity | COD | TSS |
| --- | --- | --- | --- | --- |
|  | °C | µs /cm | mg /l | mg /l |
| Initial effluent | 24 | 410 | 855 | 34 |
| Effluent after optimization | 24 | 540 | 1 177 | 48 |

### Economical evaluation

Using the economical evaluation done by ENEA for a combined UF/NF treatment on scouring waste water it can be concluded that the costs for this specific regeneration technology on a process effluent of 88 810 m³ /yr is € 0.70 /m³. This value is again a weighted average of the concerned trials as mentioned in chapter 4.5.3.

The economical data for a combined UF/NF treatment on the several dyeing process effluents as mentioned in chapter 4.5.3 lead to a weighted average of € 0.60 /m³.

Compared to the actual cost of well water of € 0.38 /m³ the UF/NF treatment cost is higher. However, as water prices will increase in the future and costs for membrane filtration units will drop, it can be expected that at a certain point the implementation of this technology will become more feasible.

## Company I06

### Production

Table 27 illustrates some production values as can be found in the PIDACS.

Table 27 : Production values I06

| Fiber | Type | Production |  | % on total |  |
| --- | --- | --- | --- | --- | --- |
| Flax | Fabric | 25 800 | kg /yr | 5 | % |
| Polyester | Fabric | 154 800 | kg /yr | 30 | % |
| Cotton/Polyester | Fabric | 167 700 | kg /yr | 32.5 | % |
| Flax/Polyester | Fabric | 83 850 | kg /yr | 16.25 | % |
| Silk/Polyester | Fabric | 83 850 | kg /yr | 16.25 | % |
| Total |  | 516 000 | kg /yr |  |  |

The total company was screened for optimization.

### Water balance

Industrial water is used for production. The water consumption equals 93 264 m³ /yr according to the PIDACS.

The industrial water consumption as obtained in the WaterTracker® scheme is 94 032 m³ /yr. This is just slightly different from the water consumption as mentioned in the PIDACS.

The detailed water balance can be found in Annex 1 and 2.

### Selection of reusable process effluents & used test results

The removal efficiency of a combined UF/NF on a mixed waste water coming from scouring, double scouring, special scouring, desizing and bleaching processes is based on the membrane filtration trials PDS/UF/NF and PS/UF/NF. The used values are illustrated in Table 28.

Table 28 : Removal efficiencies on pretreatment effluents (weighted average)

| UF/NF | Removal |  |
| --- | --- | --- |
| Organic fraction | 80 | % |
| Conductivity | 80 | % |
| TSS | 99 | % |

In addition, it is assumed that for a combined ultra- and nano-filtration plant a recovery up to 80% should be achievable.

Furthermore, the removal efficiency of a combined UF/NF on the mix of several dyeing process effluents was based on following list of membrane filtration tests:

- Direct dyeing rinsing phase:	VDDR/NF		(viscose)

- Disperse dyeing:		PDD/UF/NF	(polyester)

- Reactive dyeing:		CRD/UF/NF	(cotton)

The obtained weighted averages, based on these data are illustrated in Table 29.

Table 29 : Removal efficiencies for dyeing effluents (weighted average)

| UF/NF | Removal |  |
| --- | --- | --- |
| Organic fraction | 60 | % |
| Conductivity | 40 | % |
| TSS | 99 | % |

For the pretreatment section the selection criteria are as indicated in Table 30.

Table 30 : Selection of reusable streams preparation I06

| Criterion |  |  |
| --- | --- | --- |
| COD | < 1 000 | mg /l |
| Conductivity | < 1 000 | µS /cm |
| Other | no baths |  |

For the dyeing department the selection criteria are as indicated in Table 31.

Table 31 : Selection of reusable streams dyeing I06

| Criterion |  |  |
| --- | --- | --- |
| COD | < 1 000 | mg /l |
| Conductivity | < 1 000 | µS /cm |
| Other | no baths |  |

These criteria are similar to the values given in the methodology.

Furthermore, an anaerobic treatment is suggested as a decolourization step for the waste water coming from the reactive dyeing processes (in case of AZO-dyes).

The possible removal efficiency of an anaerobic reactor on reactive dyeing waste water was tested by LeAF. Lab trials showed that a good decolourization and a COD removal of 30% is achievable. The conductivity is assumed to be unchanged. Temperature of the anaerobic effluent will be around 35°C and the TSS of a good working reactor should be around 200 mg /l.

In order to add sufficient organic carbon to the process, high concentrated effluent from the desizing process can be mixed with the reactive dyeing waste water before adding to the anaerobic treatment.

### Obtained water savings

The industrial water consumption of the initial configuration was  94 032 m³ /yr.

Using the above selection criteria and removal efficiencies of the implemented membrane filtration technologies, the water consumption of the overall company could be reduced to 80 456 m³ /yr. This reduction equals 14.4% in total.

The water reductions for the pretreatment and dyeing department separately are respectively 27.4% and 14.3%.

Details are given in Annex 2.

### Changed contamination of process water & discharges

Table 32 summarizes the contamination of the process water for the initial and alternative scenario’s in the pretreatment department.

Table 32 : Process water quality in preparation section I06

| Stream | Temperature | Conductivity | COD | TSS |
| --- | --- | --- | --- | --- |
|  | °C | µs /cm | mg /l | mg /l |
| Process water (industrial water) | 18 | 190 | 4 | 0 |
| Permeate UF/NF | 26 | 40 | 81 | 0 |
| Mix permeate & process water | 25 | 70 | 68 | 0 |

It can be concluded that the COD of the obtained water quality, after mixing the industrial water with permeate, is slightly higher than the values mentioned in the methodology. However, tests have proven that the reuse of permeate of a combined UF/NF on scouring and bleaching process effluents in similar processes is achievable.

In addition, Table 33 summarizes the contamination of the process water for the initial and alternative scenario’s in the dyeing department.

Table 33 : Process water quality in dyeing department I06

| Stream | Temperature | Conductivity | COD | TSS |
| --- | --- | --- | --- | --- |
|  | °C | µs /cm | mg /l | mg /l |
| Process water (industrial water) | 18 | 190 | 4 | 0 |
| Permeate UF/NF | 31 | 210 | 125 | 0 |
| Mix permeate & process water | 23 | 200 | 52 | 0 |

As the water consumption decreases, the contamination of the final effluent increases.

On the other hand, when an anaerobic reactor is implemented in the scheme on some specifice process effluents, the COD of the final effluent will be reduced.

These changes are illustrated in Table 34.

Table 34 : Changed effluent concentration I06

| Stream | Temperature | Conductivity | COD | TSS |
| --- | --- | --- | --- | --- |
|  | °C | µs /cm | mg /l | mg /l |
| Initial effluent | 34 | 1 170 | 1 116 | 25 |
| Effluent after optimization | 35 | 1 370 | 1 192 | 44 |

### Economical evaluation

Using the economical evaluation done by ENEA for a combined UF/NF treatment on the mixed waste water coming from scouring, double scouring, special scouring, desizing and bleaching processes, it can be concluded that the costs for this specific regeneration technology on a small flow rate of 12 345 m³ /yr is larger than € 1 /m³.

The economical data for a combined UF/NF treatment on the several dyeing process effluents as mentioned in chapter 4.6.3 lead as well to a cost higher than € 1 /m³. This is as well due to the very small flow rate towards the filtration plant (4 624 m³ /yr).

Compared to the actual cost of industrial water of more or less € 0.3 /m³ (water + treatment cost) the UF/NF treatment cost is high.

Refering to the economical data it can be concluded from the curves that membrane filtration plants on waste water flows below 50 000 m³ /yr are at this point not achievable.

## Company I09

### Production

Table 35 illustrates some production values as can be found in the PIDACS.

Table 35 : Production values I09

| Fiber | Type | Production |  | % on total |  |
| --- | --- | --- | --- | --- | --- |
| Silk | yarn | 750 792 | kg /yr | 69.5 | % |
|  | fabric | 260 519 | kg /yr | 24 | % |
| Total |  | 1 079 773 | kg /yr |  |  |

The pretreatment department, as well as the dyeing section were screened for optimization.

### Water balance

Industrial water is used for production. The water consumption equals 291 568 m³ /yr according to the PIDACS.

This industrial water is first filtered. Water quality W6 is obtained. Part of the filtered water is softened and disinfected (quality W4). Another fraction of the filtered water is send over a heat exchanger in order to increase temperature from 11 to 25°C (quality W5).

The yearly consumption of water in the production for W4, W5 and W6 are respectively                47 939 m³ /yr, 101 741 m³ /yr and 51 664 m³ /yr.

The detailed water balance can be found in Annex 1 and 2.

### Selection of reusable process effluents & used test results

The removal efficiency of a combined UF/NF on a mixed waste water coming from scouring processes is based on the membrane filtration trials PDS/UF/NF and PS/UF/NF. The used values are illustrated in Table 36.

Table 36 : Removal efficiencies on pretreatment effluents (weighted average)

| UF/NF | Removal |  |
| --- | --- | --- |
| Organic fraction | 80 | % |
| Conductivity | 80 | % |
| TSS | 99 | % |

In addition, it is assumed that for a combined ultra- and nano-filtration plant a recovery up to 80% should be achievable.

Furthermore, the removal efficiency of a nano-filtration on a mixed dyeing waste water, consisting mainly out of acid dyeing process effluent is based on the membrane filtration trial SADR/NF.

The removal ratios are illustrated in Table 37.

Table 37 : Removal efficiencies on viscose acid dyeing effluents

| UF/NF | Removal |  |
| --- | --- | --- |
| Organic fraction | 34 | % |
| Conductivity | 45 | % |
| TSS | 99 | % |

For the pretreatment section the selection criteria are as indicated in Table 38.

Table 38 : Selection of reusable streams preparation I09

| Criterion |  |  |
| --- | --- | --- |
| COD | < 1 000 | mg /l |
| Conductivity | < 1 000 | µS /cm |
| Other | no baths |  |

For the dyeing department the selection criteria are as indicated in Table 39.

Table 39 : Selection of reusable streams dyeing I09

| Criterion |  |  |
| --- | --- | --- |
| COD | < 1 000 | mg /l |
| Conductivity | < 1 000 | µS /cm |
| Other | no baths |  |

These criteria are similar to the values given in the methodology.

### Obtained water savings

Using the above selection criteria and removal efficiencies of the implemented membrane filtration technologies, the consumption of W5 water can be reduced from 101 741 m³ /yr to 52 365 m³ /yr.

The W5 water reductions for the pretreatment and dyeing department separately are respectively 36% and 87%.

The total water reductions for the pretreatment and dyeing department separately are respectively 24% and 32%.

Details are given in Annex 2.

### Changed contamination of process water & discharges

Table 40 summarizes the contamination of the process water for the initial and alternative scenario’s in the pretreatment department.

Table 40 : Process water quality in preparation section I09

| Stream | Temperature | Conductivity | COD | TSS |
| --- | --- | --- | --- | --- |
|  | °C | µs /cm | mg /l | mg /l |
| Process water (quality W5) | 25 | 190 | 4 | 0 |
| Permeate UF/NF | 22.5 | 40 | 34 | 0 |
| Mix permeate & process water | 24 | 140 | 15 | 0 |

The obtained water quality after mixing is good. Temperature of the permeate is comparable to the temperature of the ‘warm’ process water.

In addition, Table 41 summarizes the contamination of the process water for the initial and alternative scenario’s in the dyeing department.

Table 41 : Process water quality in dyeing department I09

| Stream | Temperature | Conductivity | COD | TSS |
| --- | --- | --- | --- | --- |
|  | °C | µs /cm | mg /l | mg /l |
| Process water (industrial water) | 25 | 190 | 4 | 0 |
| Permeate UF/NF | 21 | 150 | 81 | 0 |
| Mix permeate & process water | 21.5 | 160 | 71 | 0 |

The temperature of the permeate and the process water is comparable.

The COD of the mixed stream is slightly higher than the limit as mentioned in the methodology.

As the water consumption decreases, the contamination of the final effluent increases. Due to the fact that the pretreatment and dyeing department have been evaluated separately, the changed concentration of the overall final effluent was not calculated.

### Economical evaluation

The costs of the combined UF/NF installation on the scouring waste water in the pretreatment department were calculated. Due to the fact that only a small flow of 26 588 m³ /yr is recycled the costs will be around € 1 /m³.

The economical data for a NF treatment on the acid dyeing process effluent on the other hand lead  to a cost of € 0.9 /m³. This is as well due to the very small flow rate towards the filtration plant     (35 132 m³ /yr).

Compared to the actual cost of process water quality W5 of € 0.39 /m³ (€ 0.29 water + € 0.1 treatment cost) the filtration treatment cost is still high.

In reference to the economical data it can be concluded from the curves that membrane filtration plants on waste water flows below 50 000 m³ /yr are at this point not achievable.

Increasing costs for water and decreasing costs for implementation of filtration technology should stimulate the market in the near future.

## Company I15

### Production

Table 42 illustrates some production values as can be found in the PIDACS.

Table 42 : Production values I15

| Fiber | Type | Production |  | % on total |  |
| --- | --- | --- | --- | --- | --- |
| Silk | Fabric | 1 645 132 | kg /yr | 58.73 | % |
| Polyester | Fabric | 404 466 | kg /yr | 14.44 | % |
| Synthetic | Fabric | 482 764 | kg /yr | 17.24 | % |
| Natural | Fabric | 268 680 | kg /yr | 9.59 | % |
| Total |  | 2 801 041 | kg /yr |  |  |

The following departments were screened for optimization: Preparation, Dyeing, Printing and Washing section.

### Water balance

The water used in production is a mixture of industrial and well water (water quality W3). The total water consumption for industrial and well water is respectively 351 380 m³ /yr and 224 004 m³ /yr according to the PIDACS.

Part of this water is softened before using it in production (quality W4).

According to the WaterTracker® schemes the consumption of W3 and W4 in production is respectively 398 620 m³ /yr and 275 964 m³ /yr. These values are higher than the summation of industrial and well water, due to the fact that process effluents are already recycled over an existing nano-filtration unit.

The detailed water balance can be found in Annex 1 and 2.

### Selection of reusable process effluents & used test results

The removal efficiency of a combined UF/NF on a mixed waste water coming from scouring processes is based on the membrane filtration trials PDS/UF/NF and PS/UF/NF. The used values are illustrated in Table 43.

Table 43 : Removal efficiencies on scouring effluents (weighted average)

| UF/NF | Removal |  |
| --- | --- | --- |
| Organic fraction | 80 | % |
| Conductivity | 80 | % |
| TSS | 99 | % |

It was assumed that for a combined ultra- and nano-filtration plant a recovery up to 80% should be achievable.

Furthermore, the removal efficiency of a combined UF/NF on the mix of several dyeing process effluents was based on following list of membrane filtration tests:

- Acid dyeing silk:		SADR/NF		(silk)

- Disperse dyeing:		PDD/UF/NF	(polyester)

- Reactive dyeing:		SYRD		(silk)

The removal ratios are illustrated in Table 44.

Table 44 : Removal efficiencies on mix of dyeing effluents (weighted average)

| UF/NF | Removal |  |
| --- | --- | --- |
| Organic fraction | 45 | % |
| Conductivity | 42 | % |
| TSS | 99 | % |

In addition, it was assumed that for the selected waste waters from the printing department a removal efficiency as illustrated in Table 45 can be achieved by implementing a membrane filtration plant.

Table 45 : Removal efficiencies printing effluents (assumption)

| UF/NF | Removal |  |
| --- | --- | --- |
| Organic fraction | 45 | % |
| Conductivity | 42 | % |
| TSS | 99 | % |

For the washing department the data from the membrane filtration trial PDP/UF/NF was used, as only the disperse printed washing was taken into account.

Table 46 illustrates the removal ratios.

Table 46 : Removal efficiencies disperse printed washing

| UF/NF | Removal |  |
| --- | --- | --- |
| Organic fraction | 95 | % |
| Conductivity | 58 | % |
| TSS | 99 | % |

For all the different sections the selection criteria for reusable streams are as indicated in Table 47.

Table 47 : Selection of reusable streams preparation I09

| Criterion |  |  |
| --- | --- | --- |
| COD | < 1 000 | mg /l |
| Conductivity | < 1 000 | µS /cm |
| Other | no baths |  |

These criteria are similar to the values given in the methodology.

### Obtained water savings

Using the above selection criteria and removal efficiencies of the implemented membrane filtration technologies, the consumption of W3 water can be reduced from 398 620 m³ /yr to 275 964 m³ /yr.

For the softened water, the consumption is reduced from 113 410 to 43 815 m³ /yr.

As a result, the overall reduction equals 192 251 m³ /yr or 37.8% of water consumption in production.

The water saving for the different screened units (pretreatment, dyeing, printing and washing) are respectively 69%, 36%, 30% and 42%.

Details are given in Annex 2.

### Changed contamination of process water & discharges

Table 48 summarizes the contamination of the process water for the initial and alternative scenario’s in the pretreatment department.

Table 48 : Process water quality in preparation section I15

| Stream | Temperature | Conductivity | COD | TSS |
| --- | --- | --- | --- | --- |
|  | °C | µs /cm | mg /l | mg /l |
| Process water (quality W4) | 18 | 40 | 10 | 0 |
| Permeate UF/NF | 33 | 50 | 56 | 0 |
| Mix permeate & process water | 28 | 50 | 42 | 0 |

The mixing of permeate with process water implies a slight increase of temperature.

Table 49 summarizes the contamination of the process water for the initial and alternative scenario’s in the dyeing department.

Table 49 : Process water quality in dyeing unit I15

| Stream | Temperature | Conductivity | COD | TSS |
| --- | --- | --- | --- | --- |
|  | °C | µs /cm | mg /l | mg /l |
| Process water (quality W4) | 18 | 40 | 10 | 0 |
| Permeate UF/NF | 21 | 210 | 76 | 0 |
| Mix permeate & process water | 19.5 | 130 | 44 | 0 |

The obtained water quality is good when compared to the criteria given in the methodology.

Table 50 summarizes the contamination of the process water for the initial and alternative scenario’s in the printing department.

Table 50 : Process water quality in printing section I15

| Stream | Temperature | Conductivity | COD | TSS |
| --- | --- | --- | --- | --- |
|  | °C | µs /cm | mg /l | mg /l |
| Process water (quality W3) | 16 | 400 | 10 | 0 |
| Permeate UF/NF | 20 | 470 | 75 | 0 |
| Mix permeate & process water | 17 | 420 | 30 | 0 |

The obtained water quality is good when compared to the criteria given in the methodology.

Table 51 summarizes the contamination of the process water for the initial and alternative scenario’s in the washing department.

Table 51 : Process water quality in washing department I15

| Stream | Temperature | Conductivity | COD | TSS |
| --- | --- | --- | --- | --- |
|  | °C | µs /cm | mg /l | mg /l |
| Process water (quality W3) | 16 | 400 | 10 | 0 |
| Permeate UF/NF | 43 | 140 | 11 | 0 |
| Mix permeate & process water | 38 | 190 | 11 | 0 |

The obtained water quality is good when compared to the criteria given in the methodology.

As the water consumption decreases, the contamination of the final effluent increases.

These changes are illustrated in Table 52.

Table 52 : Changed effluent concentration I15

| Stream | Temperature | Conductivity | COD | TSS |
| --- | --- | --- | --- | --- |
|  | °C | µs /cm | mg /l | mg /l |
| Initial effluent production | 24 | 1 410 | 727 | 84 |
| Effluent after optimization | 23 | 2 070 | 1 136 | 134 |

### Economical evaluation

Table 53 gives an overview of the economical evaluation of I15.

Table 53 : Economical evaluation I15

| Department | Process water |  |  | Treatment |
| --- | --- | --- | --- | --- |
|  | Quality | Saving | Cost |  |
|  |  | m³ /yr | € /m³ | € /m³ |
| Pretreatment | W4 | 61 583 | ± 0.4 | 0.7 |
| Dyeing | W4 | 8 011 | ± 0.4 | > 1 |
| Printing | W3 | 115 729 | ± 0.3 | - |
| Washing | W3 | 6 926 | ± 0.3 | > 1 |

Based on this overview it can be concluded that the treatment costs are still higher than the costs of actual used process water.

The higher the flow rate the lower the cost will be per m³ of treated water.

# General conclusions

Some important results obtained during this study are summarized again in Table 54.

Table 54 : Overview obtained results

| Company | Department | Water saving | Costs |  |
| --- | --- | --- | --- | --- |
|  |  |  | Fresh water (+ treatment) | UF/NF treatment |
|  |  | % | € /m³ | € /m³ |
| B01 | polyester | 36 | 0.12 | 1.2 |
| B04 | dyeing | 24 | 0.37 | 0.69 |
| B05 | pretreatment | 0 |  |  |
|  | dyeing | 42 | 0.75 | 0.70 |
|  | total | 23 |  |  |
| I04 | pretreatment | 33 | 0.38 | 0.70 |
|  | dyeing | 29 | 0.38 | 0.60 |
|  | total | 29 |  |  |
| I06 | pretreatment | 27 | 0.30 | > 1.00 |
|  | dyeing | 14 | 0.30 | > 1.00 |
|  | total | 14 |  |  |
| I09 | pretreatment | 24 | 0.39 | > 1.00 |
|  | dyeing | 32 | 0.39 | 0.90 |
| I15 | pretreatment | 69 | 0.40 | 0.70 |
|  | dyeing | 36 | 0.40 | > 1.00 |
|  | printing | 30 | 0.30 | - |
|  | washing | 42 | 0.30 | > 1.00 |

It can be concluded that within a pretreatment department water savings from 30 to 70% can be obtained by implementation of a regeneration technology. In dyeing sections, the savings will be within the range of 15 to 40%.

For the overall companies this would mean a reduction in water consumption between 15 and 30%. And as a result, the contamination of the final effluent will increase proportionally.

The costs for implementation of membrane filtration units are still high (> € 0.60 /m³) when compared to the actual low costs of industrial or ground water (€ 0.10 – 0.20 /m³). Only when the use of this water requires an extensive, and therefore expensive pretreatment, implementation of a regeneration technology will be economically feasible.

The difference between the costs for the regeneration plant and the actual used fresh water however is further reduced as there is an additional cost saving, due to the fact that less waste water will have to be treated  in  the end-of-pipe treatment.

In addition, it can be expected that in the near future costs of the actual used industrial or ground water will increase, permits on pumping ground water will become more stringent and prices for membrane filtration will drop, due to the increasing production of this technology.

Annex 1: Excell data sheets of all companies

Annex 2: WaterTracker® schemes of all companies

Content of Deliverable 14: Integrated methodology for waterpinch and waste water design.

Content of Deliverable 8: Data source on relaxation possibilities of process inlet water quality

Content of Deliverable 9: Optimal water re-use procedures applicable in the synthetic/silk/cotton industry.